Permit Number: 	EPR/AB3092ZE			Operator: Bryn Power Limited

Facility:	AD Facility at Gelliargwellt Farm		Form Number: 	 Air1 / 21/01/16

# Reporting of emissions to air for the period from DD/MM/YYYY to DD/MM/YYYY

| Emission Point | Substance / Parameter | Emission # Limit Value | Reference Period | Result [1] | Test Method [2] | Sample Date and Times [3] | Uncertainty [4] |
| --- | --- | --- | --- | --- | --- | --- | --- |
| A1 CHP Exhaust | Oxides of Nitrogen (NO and NO2 expressed as NO2) | 500mg/m3 | Hourly mean |  | BS EN 14792 |  |  |
|  | Carbon Monoxide | 1400mg/m3 | Hourly mean |  | BS EN 15058 |  |  |
|  | Sulphur Dioxide | 350mg/m3 | Hourly mean |  | BS EN 14791 |  |  |
|  | VOC’s | 1000mg/m3 | Hourly mean |  | BS EN 12619:1999 or 13526:2002 depending on concentration |  |  |
| A2 Flare Stack Note5 | Oxides of Nitrogen (NO and NO2 expressed as NO2) | 150mg/m3 | Hourly mean |  | BS EN 14792 |  |  |
|  | Total Volatile Organic Compounds (VOCs) | 10mg/m3 | Hourly mean |  | BS EN 12619:1999 or BS EN 13526:2002 |  |  |
|  | Carbon Monoxide | 50mg/m3 | Hourly mean |  | BS EN 15058 |  |  |

- The result given is the maximum value (or the minimum value in the case of a limit that is expressed as a minimum) obtained during the reporting period, expressed in the same terms as the emission limit value. Where the emission limit value is expressed as a range, the result is given as the ‘minimum – maximum’ measured values.

- Where an internationally recognised standard test method is used the reference number is given. Where another method that has been formally agreed with Natural Resources Wales is used, then the appropriate identifier is given. In other cases the principal technique is stated, for example gas chromatography.

- For non-continuous measurements the date and time of the sample that produced the result is given. For continuous measurements the percentage of the process operating time covered by the result is given.

- The uncertainty associated with the quoted result at the 95% confidence interval, unless otherwise stated.

[5] Monitoring of flare emissions is only necessary when the flare operated in excess of 10% of the time

Signed …………………………………………………………….  		Date………………………..

(Authorised to sign as representative of Operator)

Permit Number: 	EPR/AB3092ZE			Operator: Bryn Power Limited

Facility:	AD Facility at Gelliargwellt Farm		Form Number:	Performance1 / 21/01/16

# Reporting of other performance indicators for the period DD/MM/YYYY to DD/MM/YYYY

| Parameter |  | Units |  |
| --- | --- | --- | --- |
| Power output – Electricity |  | MWh |  |
| Energy efficiency |  | MWh/m3 biogas |  |
| Electrical energy exported to the grid |  | MWh |  |
| Electrical energy drawn from the grid |  | MWh |  |
| Water usage |  | m3 |  |
| Operational time of emergency flare |  | % of operational time |  |
| Amount of biogas combusted in the CHP unit per day |  | m3/day |  |

Operator’s comments :

Signed …………………………………………………………….  		Date………………………..

(Authorised to sign as representative of Operator)