[image: image2.png]Cyfoeth
Naturiol
Cymru

Natural
Resources
Wales





Notice of variation and consolidation with introductory note
The Environmental Permitting (England & Wales) Regulations 2016
Dŵr Cymru Cyfyngedig
Trebanos Wastewater Treatment Works 

Pheasant Road
Trebanos
SWANSEA
SA8 4DN
Variation application number

PAN-009961
Permit number
BC0016601
Trebanos Wastewater Treatment Works
Permit number BC0016601
Introductory note

This introductory note does not form a part of the notice.
The following notice gives notice of the variation and consolidation of an environmental permit.
The permit has been varied to change the Iron limits from 5000µg/l absolute to Look up Table of 4000µg/l 95%tile and 8000µg/l maximum.
The schedules specify the changes made to the permit.
The status log of a permit sets out the permitting history, including any changes to the permit reference number.  It is not backdated before 6 April 2010. 
	Status log of the permit

	Description
	Date
	Comments

	Variation determined
BC0016601/V001
	26/03/2013
	Regulator initiated variation to vary and update the permit to modern conditions. Limits set to control levels of Phosphorus and Iron.

	Application PAN-002758
(variation and consolidation)
	Duly made

19/06/2018
	Application to consolidate wastewater treatment works and settled storm permit: BP0265901 and add a second storm outlet at the final effluent outfall.

	Additional information received 
	01/10/2018
	Operating Technique provided by applicant

	Variation determined BC0016601/V002 
	31/10/2018
	Varied and consolidated permit adding EDM issued.

	Application PAN-009961

(variation)
	02/04/2020
	Application to vary the Iron limits from absolute to Look Up table and update the permit to modern conditions.

	Variation determined BC0016601/V003 
	02/07/2020
	Permit issued to Dŵr Cymru Cyfyngedig


End of introductory note
	Notice of variation and consolidation 


The Environmental Permitting (England and Wales) Regulations 2016
The Natural Resources Body for Wales (“Natural Resources Wales”) in exercise of its powers under regulation 20 of the Environmental Permitting (England and Wales) Regulations 2016 varies and consolidates
Permit number

BC0016601
issued to:

Dŵr Cymru Cyfyngedig (“the operator”)

whose registered office is
Dŵr Cymru Cyfyngedig
Pentwyn Road

Nelson
Treharris

Mid Glamorgan

CF46 6LY

company registration number 02366777
to operate a regulated facility at
Trebanos Wastewater Treatment Works

Pheasant road

Trebanos

Swansea

SA8 4DN
to the extent set out in the schedules.
The notice shall take effect from 02/07/2020
	Name
	Date

	Melissa Broad


	02/07/2020


Authorised on behalf of Natural Resources Wales
Schedule 1 

The following conditions were varied as a result of the application made by the operator:

· Conditions 3.1.1, 3.1.2, 3.1.3, 3.1.4, 3.3.9, 4.2.2, 4.3.1, 4.3.5
· Tables S 3.1, Table S 4.1
· Schedule 4
The following conditions were varied as a result of a Natural Resources Wales initiated variation:
· Conditions 3.1.5 and 3.3.9.
Schedule 2 – consolidated permit

Consolidated permit issued as a separate document. 

	Permit


The Environmental Permitting (England and Wales) Regulations 2016
Permit number 

BC0016601
This is the consolidated permit referred to in the variation and consolidation notice for application PAN-009961 authorising, 
Dŵr Cymru Cyfyngedig (“the operator”),

whose registered office is 

Pentwyn Road

Nelson

Treharris

Mid Glamorgan

CF46 6LY
company registration number 02366777
to operate a water discharge activity at

Trebanos Wastewater Treatment Works

Pheasant Road

Trebanos

Swansea

to the extent authorised by and subject to the conditions of this permit.

	Name
	Date

	 Melissa Broad
	02/07/2020


Authorised on behalf of Natural Resources Wales
Conditions
1 Management

1.1 General management

1.1.1 The operator shall manage and operate the activities):
(a) in accordance with a written management system that identifies and minimises risks of pollution so far as is reasonably practicable, including those risks arising from operations, maintenance, accidents, incidents, non-conformances and those drawn to the attention of the operator as a result of complaints; and

(b) using sufficient competent persons and resources.

1.1.2 Records demonstrating compliance with condition 1.1.1 shall be maintained. 

1.1.3 Any person having duties that are or may be affected by the matters set out in this permit shall have convenient access to a copy of the permit.

2 Operations

2.1 Permitted activities

2.1.1 The only activities authorised by the permit are the activities specified in schedule 1 table S1.1.

2.2 The site 

2.2.1 The discharge activities shall take place at the discharge points marked on the site plans at schedule 7 to this permit, and as listed in table S3.2; and, the operating technique that is the subject of conditions prefixed by 2.3 shall be applied at the locations shown, or otherwise described, in schedule 7.

2.3 Operating techniques

2.3.1 The activity shall, subject to the conditions of this permit, be operated using the techniques and in the manner described in the documentation specified in schedule 1, table S1.2, unless otherwise agreed in writing by Natural Resources Wales.

2.3.2 If notified by Natural Resources Wales that the activities are giving rise to pollution, the operator shall submit to Natural Resources Wales for approval within the period specified, a revision of any plan or other documentation (“plan”) specified in schedule 1, table S1.2 which identifies and minimises the risks of pollution relevant to that plan , and shall implement the approved revised plan in place of the original from the date of approval, unless otherwise agreed in writing by Natural Resources Wales.

2.3.3 For the activity A1 referenced in schedule 1, table S1.1 The operator shall comply with the relevant requirements of the Urban Waste Water Treatment (England and Wales) Regulations 1994.

2.3.4 
For the discharge specified in table S3.3:

(a) The discharge shall only occur when and only for as long as the flow passed forward is equal to or greater than the overflow setting indicated due to rainfall and/or snow melt.
(b) Sewage can only go to storm storage if, and for as long as, the flow of sewage is equal to or greater than the storm overflow setting due to rainfall and/or snowmelt.  

(c) Storm storage must be fully utilised before it can discharge to land or water. 

(d) The storage shall be emptied and its contents returned to the continuation flow as soon as reasonably practical. 

(e) The discharge shall not be comminuted or macerated and shall have passed through screens as specified. All screenings shall be removed from the discharge.

(f) Where a mechanically cleaned screen is installed, a telemetry alarm system shall be installed and maintained so as to give the operator immediate notification of a failure of the screen cleaning mechanism, unless otherwise agreed in writing by Natural Resources Wales. The operator shall take all appropriate measures to return the screen cleaning mechanism to normal operation as soon as reasonably practicable after receipt of notification of the failure.
2.4 Improvement programme

2.4.1 The operator shall complete the improvements specified in schedule 1 table S1.3 by the date specified in that table unless otherwise agreed in writing by Natural Resources Wales.

2.4.2 Except in the case of an improvement which consists only of a submission to Natural Resources Wales, the operator shall notify Natural Resources Wales within 14 days of completion of each improvement.

3 Emissions and monitoring

3.1 Emissions to water

3.1.1 The limits given in schedule 3 table S3.1 shall not be exceeded.

3.1.2 The limits in schedule 3 table S3.1 to which this condition applies may be exceeded where: in any series of samples of the discharge taken at regular but randomised intervals in any period of twelve consecutive months as listed in column 1 of schedule 3A, no more than the relevant number of samples, as listed in column 2 of schedule 3A, exceed the applicable limit for that relevant parameter. For relevant parameters subject to schedule 3C the assessment is based on a fixed calendar year from 1 January to 31 December inclusive.

(a) For the emission limits in schedule 3 table S3.1 to which this condition applies, no sample of the discharge taken at a time when unusual weather conditions are adversely affecting the operation of the waste water treatment works, shall be taken into account in deciding whether or not the emission limit has been complied with.

(b) On any occasion where unusual weather conditions adversely affect the operation of the waste water treatment works, the operator shall use its best endeavours to mitigate that adverse effect.

(c) For any sample of the discharge taken to be considered for the purposes of (a) above, the operator shall notify Natural Resources Wales in writing within 14 days of becoming aware that an emission limit has been exceeded. That notification shall include a full description of the unusual weather conditions and their impact on the operation of the works.

(d) For the emission limits in schedule 3 table S3.1 to which this condition applies, no sample of the discharge taken at a time when abnormal operating conditions are adversely affecting the operation of the waste water treatment works, shall be taken into account in deciding whether or not the emission limit has been complied with.

(e) On any occasion where abnormal operating conditions adversely affect the operation of the waste water treatment works, the operator shall use its best endeavours to mitigate that adverse effect.

(f) For any sample of the discharge taken to be considered for the purposes of (a) above, the operator shall notify Natural Resources Wales in writing within 14 days of becoming aware that an emission limit has been exceeded. That notification shall include a full description of the abnormal operating conditions and their impact on the operation of the works.

3.1.3 The permitted Dry Weather Flow limit in schedule 3 table S3.1 is set at the operator`s planned annual 80% exceeded daily volume discharged. 

(a) For compliance purposes an exceedance shall be recorded for a calendar year only when the limit in effect on 31 December of that calendar year is exceeded by 90% or more of the ‘good’ recorded Total Daily Volumes in that calendar year. 

(b) Until 1 January 2026 

(i) If an exceedance of the Dry Weather Flow limit is recorded in a calendar year then the operator shall, as soon as is practicable, investigate the reasons for the exceedance. 

(ii) The operator shall report the reasons for the exceedance to Natural Resources Wales and the steps that it proposes to take to restore compliance. 

(iii) An exceedance of the Dry Weather Flow limit shall not be recorded as a failure of the Dry Weather Flow limit in that calendar year if the operator takes appropriate steps to restore compliance. 

3.2 Emissions of substances not controlled by emission limits

3.2.1 For the activity A1 referenced in schedule 1, table S1.1 The operator shall take appropriate measures to minimise so far as reasonably practicable the polluting effects of the emissions of substances in the discharge not controlled by emission limits (excluding odour).

3.3 Monitoring 

3.3.1 The operator shall, unless otherwise agreed in writing by Natural Resources Wales, undertake the monitoring specified in the following tables in schedule 3 to this permit:

(a) point source emissions specified in tables S3.1 and S3.4;

(b) inlet quality specified in tables S3.1 and S3.4.

3.3.2 The operator shall maintain records of all monitoring required by this permit.

3.3.3 Monitoring equipment, techniques, personnel and organisations employed for the emissions monitoring programme specified in condition 3.3.1 shall have either MCERTS certification or MCERTS accreditation (as appropriate), where available, unless otherwise agreed in writing by Natural Resources Wales.

3.3.4 Accessible monitoring points shall be provided and maintained to enable the emissions monitoring programme to be carried out at the monitoring points specified in table S3.4 of schedule 3 and shown marked on the site plans in schedule 7. 

3.3.5 The monitoring programme for the parameters subject to schedule 3B shall be:

(a) pre-scheduled to cover a calendar year and the programme recorded before the start of a calendar year sample period; and

(b) spot samples collected at approximately equal intervals during the year, including samples from different days of the week and different times.  Approximately 10% of samples should be outside the normal sampling window which is 9am-3pm, Monday to Friday.

3.3.6 After becoming aware, or following a notification that a sample has not been taken on the schedule 3B Monitoring Programme pre-scheduled date, or is lost, or a result for that sample cannot be reported, the operator shall record the details and reschedule the sample.
3.3.7 The monitoring programme for the parameters subject to schedule 3C shall be: 

(a) pre-scheduled before each calendar year; 

(b) Unless otherwise agreed in writing by Natural Resources Wales, the operator shall submit the monitoring programme for the following calendar year to Natural Resources Wales before the 1st of December; and 

(c) samples must be collected at approximately equal intervals during the year from different days of the week and approximately 10% of samples should be taken at weekends. 
3.3.8   Unless otherwise agreed in writing by Natural Resources Wales, after becoming aware, or following notification that a sample has not been taken on the schedule 3C Monitoring Programme pre-scheduled date, or is lost, or a result for that sample cannot be reported, the operator shall notify Natural Resources Wales of the missed even and the reschedule date as soon as reasonably practicable. 

3.3.9
The Operator shall take appropriate measures to ensure that the event recorder remains fully operational at all times within the reference period specified in table S3.1. Any failures shall be remedied as soon as reasonably practicable.
4 Information

4.1 Records

4.1.1 All records required to be made by schedule 3, 4 and 5 to this permit shall:

(a) be legible;

(b) be made as soon as reasonably practicable;

(c) if amended, be amended in such a way that the original and any subsequent amendments remain legible, or are capable of retrieval; and

(d) be retained, unless otherwise agreed in writing by Natural Resources Wales, for at least 10 years from the date when the records were made. 

4.1.2 The operator shall maintain convenient access, in either electronic or hard copy, to the records, plan and management system required to be maintained by this permit. 
4.2 Reporting

4.2.1 The operator shall send all reports and notifications required by the permit to Natural Resources Wales using the contact details supplied in writing by Natural Resources Wales.

4.2.2 Within the time period after the end of the reporting period specified in schedule 4 table S4.1 the operator shall, unless otherwise agreed in writing by Natural Resources Wales, submit reports of the monitoring and assessment carried out in accordance with the conditions of this permit, as follows:

(a) in respect of the parameters and monitoring points specified in schedule 4 table S4.1;

(b) [for the reporting periods specified in schedule 4 table S4.1 and using the forms specified in schedule 4 table S4.2; and

(c) giving the information from such results and assessments as may be required by the forms specified in those tables.

4.3 Notifications

4.3.1 Natural Resources Wales shall be notified as soon as reasonably practicable following detection, within the site of the regulated facility of:

(a) any malfunction, breakdown or failure of equipment or techniques, accident, or emission of a substance not controlled by an emission limit which has caused, is causing or may cause significant pollution; and

(b) any breach of a limit specified in schedule 3 table S3.1 (including individual exceedances of limits which are covered by condition 3.1.2).

Any other significant adverse environmental effects, which may have been caused by the activity, shall also be notified to Natural Resources Wales as soon as reasonably practicable following detection.

4.3.2 The information provided under condition 4.3.1 shall be supported by sending the information listed in schedule 5 to this permit within the time period specified in that schedule.

4.3.3 Where Natural Resources Wales has requested in writing that it shall be notified when the operator is to undertake monitoring and/or spot sampling specified in schedule [3B/3C], the operator shall inform Natural Resources Wales when the relevant monitoring and/or spot sampling is to take place. The operator shall provide this information to Natural Resources Wales at least 14 days before the date the monitoring is to be undertaken.

4.3.4 Natural Resources Wales shall be notified within 14 days of the occurrence of the following matters, except where such disclosure is prohibited by Stock Exchange rules:

Where the operator is a registered company:

(a) any change in the operator’s trading name, registered name or registered office address; and

(b) any steps taken with a view to the operator going into administration, entering into a company voluntary arrangement or being wound up.

Where the operator is a corporate body other than a registered company:

(c) any change in the operator’s name or address; and

(d) any steps taken with a view to the dissolution of the operator.

4.3.5 For the activity A1 referenced in schedule 1, table S1.1 where the operator proposes to make a change in the nature of the activity by increasing the concentration of, or the addition of, or allowing the introduction of, a substance to the activity to an extent that the operator considers could have a significant adverse environmental effect on the receiving waters, and the change is not permitted by emission limits specified within schedule 3 table S3.1 or the subject of an application for approval under the EP Regulations or under the terms of this permit:

(a) Natural Resources Wales shall be notified in writing at least 14 days before the increase or addition or allowing the introduction; and

(b) the notification shall contain a description of the proposed change.

4.3.6 For the activity A1 referenced in schedule 1, table S1.1 the operator shall inform Natural Resources Wales in writing of any change, or proposed change, to the population equivalent such as would make a material change to the application of the Regulations and shall, on request, inform the Natural Resources Wales in writing of the actual population equivalent. 

4.4 Interpretation

4.4.1 In this permit the expressions listed in schedule 6 shall have the meaning given in that schedule.

4.4.2 In this permit references to reports and notifications mean written reports and notifications, except where reference is made to notification being made “as soon as reasonably practicable”, in which case it may be provided by telephone.
Schedule 1 – Operations 
	Table S1.1 Activities

	Activity reference
	Description of activity
	Limits of specified activity

	A1
	Discharge of secondary treated sewage via Outlet 2
	N/A

	A2
	Discharge of settled storm sewage via Outlets 1 and 2
	Storm effluent will discharge via the final effluent line where there is capacity. When the new pump is beaten, settle storm effluent will spill from the tank down the existing storm link at Outlet 1.


	Table S1.2 Operating techniques

	Description of documentation
	Parts
	Date Received

	Application
	Trebanos – Storm Operating Condition
	01/10/2018


	Table S1.3 Improvement programme requirements

	Reference
	Requirement
	Date

	Discharge of storm sewage via Outlets 1 and 2
	The Operator will have designed a solution which ensures that the discharge of settled storm effluent from the storm system only occurs when the Tawe offers sufficient dilution at the discharge point.
	31/10/2020


Schedule 2 – Waste types, raw materials and fuels

Schedule 2 not in use.

Schedule 3 – Emissions and monitoring
	Table S3.1 Point Source emissions to water (other than sewer) – emission limits and monitoring requirements

	Effluent and discharge point
	Parameter  
	Limit (including unit)
	Reference Period
	Limit of effective range
	Monitoring frequency
	Compliance Statistic

	A1 Secondary treated sewage effluent via Outlet 2
	Dry weather flow
	6290 m3/day


	Total daily volume
	N/A                                                                
	Continuous
	Condition 3.1.5 

	
	15-minute instantaneous or averaged flow
	No limit set. Record as l/s
	15 minute
	N/A
	Continuous
	N/A

	
	ATU-BOD as O2
	40 mg/l
	Instantaneous (spot sample)
	N/A
	As specified in schedule 3B
	Look up table

(Conditions 3.1.2 and 3.1.3 apply)

	
	ATU-BOD as O2
	80 mg/l
	Instantaneous (spot sample)
	N/A
	As specified in schedule 3B
	Maximum

(Condition 3.1.3 applies)

	
	Ammoniacal nitrogen (expressed as N)
	25 mg/l
	Instantaneous (spot sample)
	N/A
	As specified in schedule 3B
	Look up table

(Conditions 3.1.2 and 3.1.3 apply)

	
	Ammoniacal nitrogen (expressed as N)
	50 mg/l
	Instantaneous (spot sample)
	N/A
	As specified in schedule 3B
	Maximum

(Condition 3.1.3 applies)

	
	Suspended solids (measured after drying at 105oC)


	45 mg/l
	Instantaneous (spot sample)
	N/A
	As specified in schedule 3B
	Look up table

(Conditions 3.1.2 and 3.1.3 apply)

	
	Total iron as Fe
	4000 µg/l
	Instantaneous (spot sample)
	N/A
	As specified in schedule 3B
	Look up table

(Conditions 3.1.2 and 3.1.3 apply)

	
	Total iron as Fe
	8000 µg/l
	Instantaneous (spot sample)
	N/A
	As specified in schedule 3B
	Maximum

(Condition 3.1.3 applies)

	
	Visible oil or grease
	No significant trace present so far as is reasonably practicable
	Instantaneous (visual examination )
	N/A
	N/A
	No significant trace

(Condition 3.1.3 applies)

	
	ATU-BOD as O2  (UWWTR)
	Minimum of 70 % removal compared to influent
	24 hour composite
	To be compliant a sample has to meet the 70% removal standard or the 25 mg/l limit not both 
	As specified in schedule 3C 
	Look up table

(Conditions 3.1.2 and 3.1.4 apply) 

	
	ATU-BOD as O2  (UWWTR)
	25 mg/l
	
	
	
	

	
	ATU-BOD as O2  (UWWTR)
	50 mg/l
	24 hour composite
	This limit does not apply if a sample has met the 70% removal standard
	As specified in schedule 3C


	Maximum

(Condition 3.1.4 applies)

	
	COD as O2 (UWWTR)
	Minimum of 75 % removal compared to influent
	24 hour composite
	To be compliant a sample has to meet the 75% removal standard or the 125 mg/l limit not both 
	As specified in schedule 3C
	Look up table

(Conditions 3.1.2 and 3.1.4 apply) 

	
	COD as O2 (UWWTR)
	125 mg/l
	
	
	
	

	
	COD as O2 (UWWTR)
	250 mg/l
	24 hour composite
	This limit does not apply if a sample has met the 75% removal standard 
	As specified in schedule 3C


	Maximum

(Condition 3.1.4 applies)

	
	Total phosphorus as P (UWWTR)
	2mg/l
	24 hour composite
	To be compliant the discharge has to meet the 80% removal standard or the 2 mg/l limit not both 


	As specified in schedule 3C
	Annual mean 

(Condition 3.1.4 applies)

	A2 Storm sewage 


	Block counted spills 
	N/A
	1st January to 31st December inclusive 
	N/A
	15 minutes
	N/A

	
	Event recorder status operational 
	N/A
	N/A
	N/A
	15 minutes
	N/A

	
	Discharge start and end times
	N/A
	N/A
	Condition 3.3.3 does not apply
	Whenever a discharge occurs
	N/A


	Table S3.2 Discharge points

	Effluent Name
	Discharge Point
	Discharge point NGR
	Receiving water

	A1 Secondary treated sewage effluent 
	Outlet 2
	SN 70879 02128
	River Tawe

	A2 Settled storm sewage
	Outlet 1 or Outlet 2
	SN 71197 02214
(Outlet 1) 
	River Tawe


	Table S3.3 Storm sewage discharge settings

	Effluent and discharge point 
	Description of discharge
	Overflow setting l/s
	Maximum size of solid matter
	Screen aperture

size
	Minimum screen capacity flow l/s
	Minimum  storage capacity m3 (off-line)

	A2 Settled storm sewage 
	Settled storm sewage
	146
	No greater than 10 mm in more than 2 dimensions 

	10mm (bar screen)

	All flows shall be screened 

	1200


	Table S3.4 Monitoring points

	Effluents and discharge points
	Monitoring type
	Monitoring point NGR
	Monitoring point reference

	A1 Secondary treated sewage effluent via Outlet 2
	UWWTR Inlet sampling point
	SN 71224 02407
	UWW & EDM Monitor 1 Inlet Sample Point

	
	Final Effluent sampling 
	SN 71190 02300
	Secondary Treated Sewage Effluent Sample Point

	
	UWWTR outlet sampling point
	SN 71190 02300
	UWW sample point

	
	Flow monitoring point
	SN 71164 02257
	MCERT and EDM Monitor 3

	A2 Settled storm sewage via Outlet 1
	Storm Effluent sampling
	SN 71177 02225
	Outlet 1 Storm Sewage Sample Point

	
	Event duration monitoring
	SN 71169 02234
	EDM Monitor 2 Sample Point

	A3 Settled storm sewage via Outlet 2
	Storm Effluent sampling
	SN 71151 02238
	Outlet 2 Settled Storm sample point

	
	Event duration monitoring
	SN 71164 02257
	MCERT and EDM Monitor 3


Schedule 3A - Look up table

	Look up table

	Number of samples taken in any period of 12 months
	Maximum number of samples permitted to exceed limit for given parameter

	4–7  
	 1

	8–16
	 2

	17–28 
	 3

	29–40 
	 4

	41–53  
	 5

	54–67  
	 6

	68–81  
	 7

	82–95 
	 8

	96–110 
	 9

	111–125  
	 10

	126–140  
	 11

	141–155  
	 12

	156–171  
	 13

	172–187 
	 14

	188–203  
	 15

	204–219  
	 16

	220–235  
	 17

	236–251 
	 18

	252–268 
	 19

	269–284  
	 20

	285–300  
	 21

	301–317 
	 22

	318–334  
	 23

	335–350 
	 24

	351–365 
	 25


Schedule 3B - OSM tier 3 sampling frequency

	Parameter
	‘Normal frequency’ of samples per year
	Reduced Sampling frequency after 12 consecutive months of numeric permit compliance, samples per year or pro rata over the remainder of a year
	On numeric limit failure return to normal frequency as soon as reasonably practicable, samples per 12 months
	Out of hours samples

	Sanitary


	24
	12
	24
	For 24 samples 2 out of hours samples per annum

	Non sanitary


	12
	12
	12
	For 12 samples 1 out of hours sample per annum


Schedule 3C – Urban Waste Water Treatment Regulations sampling frequency

	Population equivalent
	Samples per year
	Reduced sampling frequency after a year without an UWWTR exceedance or failure, samples per year
	Following an UWWTR exceedance or failure return to the higher frequency in the year that follows, samples per year

	2,000 to 9,999

	12
	4
	12

	10,000 to 49,999

	12
	N/A
	N/A

	50,000 or over

	24
	N/A
	N/A


Schedule 4 – Reporting

Parameters, for which reports shall be made, in accordance with conditions of this permit, are listed below.

	Table S4.1 Reporting of monitoring data

	Parameter
	Monitoring point reference
	Reporting period
	Period begins

	Dry Weather Flow (daily flows total)
	FE & UWW sample point
	Annually

Report to be submitted within 2 months of the end of the calendar year
	1 January

	15-minute flow
	FE & UWW sample point
	Reports to be provided to Natural Resources Wales upon request 

Report to be submitted within 28 days unless otherwise specified in writing by Natural Resources Wales
	Upon request by Natural Resources Wales

	UWWTR - ATU-BOD as O2, COD as O2, total phosphorus as P
	UWW Inlet sample point
	Monthly

Report to be submitted within 28 days
	1st of month

	Operator Self Monitoring - ATU-BOD as O2, ammoniacal nitrogen (expressed as N), suspended solids (measured after drying at 105oC), total iron as Fe
	FE & UWW sample point
	Quarterly

Report to be submitted within 28 days
	1st of month

	Operator Self Monitoring 
	FE & UWW sample point
	Annually

Report to be submitted within 2 months of the end of the calendar year
	1 January

	Settled storm performance, including adjusted number of total spills


	Settled Storm Sample Point
	Annually

Report to be submitted within 2 months
	1 January

	Duration of total spills


	Settled Storm Sample Point
	Annually

Report to be submitted within 2 months
	1 January

	Event recorder status operational


	Settled Storm Sample Point
	Annually

Report to be submitted within 2 months
	1 January

	Storm sewage discharge start and end times


	Settled Storm Sample Point
	Reports to be provided to Natural Resources Wales upon request 
	As specified by Natural Resources Wales


	Table S4.2 Reporting forms

	Parameter
	Reporting format

	Dry Weather Flow (daily flows total)
	WISKI electronic format specified by Natural Resources Wales

	15-minute flow
	WISKI electronic format specified by Natural Resources Wales

	Flow to storm tank (Flow 4) Monitoring
	WISKI electronic format specified by Natural Resources Wales, 

on request, form as agreed in writing by Natural Resources Wales

	UWWTR – ATU-BOD as O2, COD as O2, total phosphorus as P, 
	Electronic format specified by Natural Resources Wales

	OSM - ATU-BOD as O2, ammoniacal nitrogen (expressed as N), suspended solids (measured after drying at 105oC), total iron as Fe
	Quarterly - Electronic format specified by Natural Resources Wales 

	Operator Self Monitoring summary report
	Annually - Summary report of compliance with the monitoring programme specified in Table 3.1 and schedule 3B in a format specified by Natural Resources Wales  

	Settled storm performance including number and duration of block counted spills
	Annual summary report or other form as agreed in writing by Natural Resources Wales



	Storm sewage discharge start and end times
	Form as agreed in writing by Natural Resources Wales 

	Event recorder status
	Annual summary report or other form as agreed in writing by Natural Resources Wales

Percentage of time in the recording period that event duration monitoring equipment is operational

	Investigation into the operation of the overflow
	Electronic format as agreed in writing by Natural Resources Wales. 


Schedule 5 – Notification 

These pages outline the information that the operator must provide. 

Units of measurement used in information supplied under Part A and B requirements shall be appropriate to the circumstances of the emission. Where appropriate, a comparison should be made of actual emissions and authorised emission limits.

If any information is considered commercially confidential, it should be separated from non-confidential information, supplied on a separate sheet and accompanied by an application for commercial confidentiality under the provisions of the EP Regulations.

Part A

	Permit Number
	BC0016601

	Name of operator
	

	Location of Facility
	Trebanos Wastewater Treatment Works

	Time and date of the detection 
	


	(a) Notification requirements for any malfunction, breakdown or failure of equipment or techniques,  accident, or emission of a substance not controlled by an emission limit which has caused, is causing or may cause significant pollution

	To be notified within 7 days of detection unless otherwise agreed in writing by the Natural Resources Wales.

	Date and time of the event
	

	Reference or description of the location of the event 
	

	Description of where any release into the environment took place
	

	Substances(s) potentially released/type or nature of sewage released
	

	Best estimate of the quantity or rate of release of substances and/or duration of discharge
	

	Best estimate of the environmental impact of the discharge
	

	Measures taken, or intended to be taken, to stop any emission
	

	Description of the failure or accident.
	


	(b) Notification requirements for the breach of a limit specified in schedule 3 table S3.1 (including individual exceedances of limits which are covered by condition 3.1.2)

	The information specified below is to be notified to Natural Resources Wales as soon as reasonably practicable following detection.

	Monitoring point reference/ source
	

	Self monitoring regime (where relevant)
	e.g. OSM/UWWTR



	Type of failure 
	e.g. LUT failure/LUT exceedance/upper tier/other



	Date of sample/event
	

	Parameter
	

	Result and units
	

	Limit and units
	


	(c) Notification requirements for the detection of any significant adverse environmental effect

	To be notified within 24 hours of detection

	Description of where the effect on the environment was detected
	

	Substances(s) detected
	

	Concentrations of substances detected
	

	Date of monitoring/sampling
	


Part B – to be submitted as soon as reasonably practicable unless otherwise agreed in writing by Natural Resources Wales

	Any more accurate information on the matters for notification under Part A.
	

	Measures taken, or intended to be taken, to prevent a recurrence of the incident/breach/exceedance
	

	Measures taken, or intended to be taken, to rectify, limit or prevent any pollution of the environment which has been or may be caused by the emission
	


	Name*
	

	Post
	

	Signature
	

	Date
	


* authorised to sign on behalf of the operator

Schedule 6 – Interpretation 

“abnormal operating conditions” include but are not limited to, the circumstances described in Regulation 40(1) of, or paragraph 6(5) of Schedule 21 to, the Environmental Permitting Regulations 2016 (illegal discharge to sewer), unusual weather, or during a defined period where the permit authorising the permitted activity has been varied for reasons such as capital works construction.
“accident” means an accident that may result in pollution.

"annually" means once every year.

“application” means the application for this permit, together with any additional information supplied by the operator as part of the application and any response to a notice served under Schedule 5 to the EP Regulations.

For the activities A1 to A2 referenced in schedule 1, table S1.1 “appropriate measures” for the purposes of the emission of substances not controlled by emission limits condition (condition 3.2.1) do not require the operator to undertake treatment to a level beyond that specified in schedule 1 table S1.1, or to carry out routine monitoring for substances not controlled by emission limits.

“ATU-BOD as O2” means the biochemical oxygen demand (measured after 5 days at 20oC with nitrification suppressed by the addition of allylthiourea).

“COD as O2” means the chemical oxygen demand (measured using the standard dichromate procedure).

“emissions of substances not controlled by emission limits” means emissions of substances to air, water or land from the permitted activities, which are not controlled by an emission limit.

“EP Regulations” means The Environmental Permitting (England and Wales) Regulations SI 2016 No.1154 and words and expressions used in this permit which are also used in the Regulations have the same meanings as in those Regulations.

"event recorder" a recorder which records the start time and end time of individual overflow events.
“MCERTS” means the Natural Resources Wales’ Monitoring Certification Scheme.

“minimum screen capacity flow” means the minimum flow passed through the screens to the outfall when the screen bypass operates. 

“monitoring frequency” as used in Table S3.1 in the context of event duration monitoring is the temporal interval at which a change in state between no discharge and discharge is to be detected.

“Natural Resources Wales” means the Natural Resources Body for Wales established by article 3 of the Natural Resources Body for Wales (Establishment) Order 2012. The Natural Resources Body for Wales (Functions) Order 2013 transferred the relevant functions of the Countryside Council for Wales, and functions of the Environment Agency and the Forestry Commission in Wales to the Natural Resources Body for Wales.

“overflow” for the purposes of schedule 7, overflow means the weir or orifice or other control which directs excess flow away from the continuation sewer when the flow exceeds the overflow setting due to rainfall and/or snowmelt.

“overflow setting” means the minimum flow passed forward to the continuation sewer when the overflow operates.

"quarter" means a calendar year quarter commencing on 1 January, 1 April, 1 July or 1 October.

“significant pollution” means a high level impact incident as indicated by NRW incident classification system.
“unusual weather conditions” includes, but is not limited to:

· low ambient temperatures, or the freezing of mechanical equipment in the works;

· significant snow deposits;

· tidal or fluvial flooding;

· weather conditions causing unforeseen loss of power supply to the sewage treatment that could not be ameliorated by the reasonable provision and operation of standby generation facilities.
“Urban Waste Water Treatment (England and Wales) Regulations 1994 (UWWTR)” means Urban Waste Water Treatment (England and Wales) Regulations 1994 SI 2841and the words and expressions used in this permit which are also used in the Regulations have the same meanings as in those Regulations.

“year” means calendar year ending 31 December.
Schedule 7 – Site plan
[image: image1.emf]
© Crown Copyright and database right 2020. Ordnance Survey licence number 100019741.

END OF PERMIT

	Variation and consolidation application number BC0016601 PAN-009961
	Page i
-  -
- i -
- i -i



