Ein cyf/Our ref: BP0006101 Eich cyf/Your ref: Natural Resources Wales Welsh Assembly Government, Rhodfa Padarn, Llanbadarn Fawr, Aberystwyth, Ceredigion, SY23 3UR Ebost/Email: callum.Stone@cyfoethnaturiolcymru.gov.uk Ffôn/Phone: 03000653405

FAO Site Manager,

Patch Caravan Park,
Gwbert,
Cardigan,

Ceredigion,

SA43 1PP,

28/09/2018

For the attention of the site manager,

RE: Patch Caravan Park Private Sewage Treatment Works (BP0006101)

Following the sample taken from Patch Caravan Sewage Treatment Works (Permit number BP0006101) taken on the 5th of September 2018, it has become evident that there is an issue with your treatment works and sewage is not being treated to the standard required to prevent environmental damage occurring as a result of the discharge.

I’ve gone through results of samples taken over the last 3 years (shown below), and during the summer months Biological Oxygen Demand (BOD), Ammonia and Suspended Solid all increase significantly which is indicative that the treatment works aren’t operating as they should be, and potentially pose an environmental risk.

| Date/Time (sampling) | BOD ATU (mg/l) | Ammonia(N) (mg/l) | Suspended Solids (mg/l) |
| --- | --- | --- | --- |
| 17/05/2016 14:11 | 3.04 | 2.38 | 25.5 |
| 31/08/2016 13:20 | 5.03 | 35.6 | 8 |
| 10/08/2017 12:45 | 73.2 | 89.8 | 55 |
| 07/11/2017 12:30 | 2.09 | 7.95 | 9 |
| 05/09/2018 13:31 | 33.7 | 104 | 22.5 |

It would be very useful if you could give me a ring at your earliest convenience so that we can discuss what course of action needs to be taken to investigate any problems with the works and potential remedies.The number you can contact me on is 03000 653405.

# Kind Regards,

CALLUM STONE

Swyddog yr Amgylchedd/Environment Officer (Ceredigion)