|  |  |  |  | DCWW-4791-S-201-MMB-06-XX-RP-NX-10310 |
| --- | --- | --- | --- | --- |
|  | Schedule 5 responses/Main supporting document draft - Five Fords v5 28 Nov 2018 - addendum.docx |  |  |  |
|  | Mott MacDonald |  |  |  |

Mott MacDonald Victory House Trafalgar Place Brighton BN1 4FY United Kingdom

T +44 (0)1273 365000

F +44 (0)1273 365100

mottmac.com

Application to vary an installation permit to include waste operation as a DAA

Five Fords AAD facility

28 November 2018

Mott MacDonald Limited. Registered in England and Wales no. 1243967. Registered office: Mott MacDonald House, 8-10 Sydenham Road, Croydon CR0 2EE, United Kingdom

Issue and Revision Record

| Revision | Date | Originator | Checker | Approver | Description |
| --- | --- | --- | --- | --- | --- |
| 1A | 11 May 2018 | Anita Manns Alex Symeonidis | David Dray |  | First draft for submission for client comment |
| 1B |  | Anita Manns Alex Symeonidis | David Dray |  | Draft for internal review |
| 2 |  | Anita Manns Alex Symeonidis | David Dray | David Dray | Final for submission |
| 3 |  | Anita Manns | David Dray | David Dray | Amended based on request from EA. |
| 4 |  | Anita Manns | David Dray | David Dray | Amended based on request from EA. |
| 5 |  | Anita Manns | David Dray | David Dray | Amended based on error found in AQ report |

| Document reference: | DCWW-4791-S-201-MMB-06-XX-RP-NX-10310 |
| --- | --- |

| Information class: | Standard |
| --- | --- |

This document is issued for the party which commissioned it and for specific purposes connected with the above-captioned project only. It should not be relied upon by any other party or used for any other purpose. We accept no responsibility for the consequences of this document being relied upon by any other party, or being used for any other purpose, or containing any error or omission which is due to an error or omission in data supplied to us by other parties. This document contains confidential information and proprietary intellectual property. It should not be shown to other parties without consent from us and from the party which commissioned it.

This report has been prepared solely for use by the party which commissioned it (the ‘Client’) in connection with the captioned project. It should not be used for any other purpose. No person other than the Client or any party who has expressly agreed terms of reliance with us (the ‘Recipient(s)’) may rely on the content, information or any views expressed in the report. We accept no duty of care, responsibility or liability to any other recipient of this document. This report is confidential and contains proprietary intellectual property. No representation, warranty or undertaking, express or implied, is made and no responsibility or liability is accepted by us to any party other than the Client or any Recipient(s), as to the accuracy or completeness of the information contained in this report. For the avoidance of doubt this report does not in any way purport to include any legal, insurance or financial advice or opinion. We disclaim all and any liability whether arising in tort or contract or otherwise which it might otherwise have to any party other than the Client or the Recipient(s), in respect of this report, or any information attributed to it. We accept no responsibility for any error or omission in the report which is due to an error or omission in data, information or statements supplied to us by other parties including the client (‘Data’). We have not independently verified such Data and have assumed it to be accurate, complete, reliable and current as of the date of such information. Forecasts presented in this document were prepared using Data and the report is dependent or based on Data. Inevitably, some of the assumptions used to develop the forecasts will not be realised and unanticipated events and circumstances may occur. Consequently Mott MacDonald does not guarantee or warrant the conclusions contained in the report as there are likely to be differences between the forecasts and the actual results and those differences may be material. While we consider that the information and opinions given in this report are sound all parties must rely on their own skill and judgement when making use of it. Under no circumstances may this report or any extract or summary thereof be used in connection with any public or private securities offering including any related memorandum or prospectus for any securities offering or stock exchange listing or announcement.

Contents

Main supporting document Non-Technical Summary 1 1 Introduction 4 1.1 Overview 4 1.2 Document content and structure 4 2 General – Varying a bespoke permit (part C2) 6 2.1 About the permit (Question 1) 6 2.2 Existing Activities 6 2.2.1 Existing Permitted Plant 7 2.2.2 Existing sludge treatment and anaerobic digestion 7 2.3 Changes to existing activities 8 2.3.1 Changes to existing gas to grid facility (within current permit boundary) 8 2.3.2 Changes to sludge treatment and anaerobic digestion (currently outside the permit boundary) 8 2.3.3 Equipment to be installed 10 2.4 Ability as an operator (Question 3) 12 2.4.1 Relevant offences (3a) 12 2.4.2 Technical ability (3b) 13 2.4.3 Finances (3c) 14 2.4.4 Management systems (3d) 14 2.5 Supporting information (Question 5) 16 2.6 Environmental Risk Assessment (Question 6) 17 2.6.1 Introduction 17 2.6.2 Impact Assessment 17 3 Part C3 – Variation to a bespoke installation permit 23 3.1 Activities applying to vary (Question 1) 23 3.1.1 Types of activity applied for 23 3.1.2 Types of waste accepted 25 3.2 Emissions to air, land and water (Question 2) 25 3.2.1 Introduction 25 3.2.2 Point source emissions to air 25 3.2.3 Point source emissions to water 28 3.2.4 Point source emissions to land 30 3.3 Operating techniques (Question 3) 30 3.3.1 Introduction 30 3.3.2 Technical standards (Question 3a) 30 3.3.3 General requirements (Question 3b) 31 3.3.4 Type and amounts of raw materials (Question 3c) 32 3.3.5 Information for specific sectors (if needed) (Question 3d) 32 3.3.6 Monitoring (Question 4) 33 3.3.7 Resource efficiency and climate change (Question 6) 34 4 Part F1 – OPRA, charges and declarations 38 4.1 Working out charges (Question 1) 38 4.2 Payment (Questions 3) 38 4.3 Confidentiality and National Security (Question 5) 38 4.4 Application Checklist (Question 6) 38 Appendices 40 A. Permit Application forms 42 B. EP OPRA 44 C. Environmental Risk Assessment 46 D. Site Plans 48 D.1 Site Location with Permitted Boundary 48 D.2 Site Boundary and Emission Points 50 E. Site Condition Report 52 F. Correspondence 54 G. Environmental Assessments 56 H. Schematics 58

Abbreviations and Acronyms

AAD: Advanced Anaerobic Digestion

AD: Anaerobic Digestion

ASP: Activated Sludge Plant

BAS: Biosolids Assurance Scheme

BAT: Best Available Techniques

BIP: Biomethane Injection Plant

BUP: Biogas Upgrading Plant

CABWI: Certification and Assessment Board for the Water Industry

CC: Complaint Commission

CHP: Combined Heat and Power

CHPQA: Combined Heat and Power Quality Assurance

COSHH: Control of Substances Hazardous to Health

CPNI: Centre for the Protection of National Infrastructure

DAA: Directly Associated Activity

DAWA: Directly Associated Waste Activity

dB(A): Decibels (A-weighted)

DCWW: Dŵr Cymru Welsh Water

DG7: Minimum standard for companies responding to written complaints

DS: Dry Solids

EA: Environment Agency

ELV: Emission Limit Values

EMP: Environmental Management Plan

EMS: Environmental Management System

EP OPRA: Environmental Protection Operator and Pollution Risk Appraisal

EPR: Environmental Permitting Regulations

ERA: Environmental Risk Assessment

HACCP: Hazards Analysis and Critical Control Points

HTH: High Temperature Heated

HYBAS: Hybrid Activated Sludge (proprietary Veolia wastewater treatment technology)

IBC: Intermediate Bulk Container

IEC: International Electrotechnical Commission

ISO: International Organisation for Standardisation

LTH: Low Temperature Heated

LTHW: Low Temperature Hot Water

LTP: Liquor Treatment Plant

LWS: Local Wildlife Site

MCERTS: Monitoring Certification Scheme (of the EA)

MWth: Megawatts thermal

NOx: Nitrogen Oxides

NRW: Natural Resources Wales

OCU: Odour Control Unit

OFGEM: Office of Gas and Electricity Markets

OFWAT: Water Services Regulation Authority (previously Office of Water Services)

OPRA: Operator and Pollution Risk Appraisal

PEA: Preliminary Ecological Appraisal

PIA: Pollution Incident Advisor

PS: Pumping Station

PVC: Polyvinylchloride

QM: Quality Manual

QMS: Quality Management System

RHI: Renewable Heat Incentive

RO: Reverse Osmosis? Responsible Officer

SAP: Systeme, Anwendungen und Produkte in der Datenverarbeitung (German multinational software supplier)

SCR: Site Condition Report

STP: Sludge Treatment Plant

T21: Treatment Exemption no 21 type of permit allowing waste recovery at a WwTW

tDS: tonnes Dry Solids

TGN: Technical Guidance Note

THP: Thermal Hydrolysis Process

TRIAD: A system through which the National Grid charges businesses for the costs associated with the electrical transmission network.

UV: Ultraviolet

VOC: Volatile Organic Compounds

WwTW: Wastewater Treatment Works

Main supporting document Non-Technical Summary

Introduction

- The Non-technical summary has been written to support the application to vary the existing bespoke Environmental Permit (EPR/AP3139FT) for the Facility on behalf of Dŵr Cymru Welsh Water (DCWW) (‘the Operator’). In order to satisfy the requirements of the Environmental Permitting Regulations (EPR) 2016, the Operator must apply to the Natural Resource Wales (NRW) for a change (variation) to an existing Environmental Permit.

- The permit variation is required to take account of the proposed changes at the wider Five Fords site, which include the addition of an Advanced Anaerobic Digestion (AAD) facility to the current Anaerobic Digestion (AD) process which takes place at the site. As part of this change, the AAD and sludge treatment processes will require the importation of an increased amount of sludge and cake from other Wastewater Treatment Works (WwTW) satellite sites around North Wales.  This will cause Five Fords to subsequently exceed the current T21 exemption (recover wastes at a wastewater treatment works), which covers the site and allows the treatment of up to 100,000 cubic metres of waste over any 12-month period.

Overview

Five Fords Wastewater Treatment Works (WwTW) is located to the south-east of Wrexham. Currently the site undertakes anaerobic digestion of sewage sludge from the on-site Five Fords WwTW, and liquid imports from other satellite WwTW sites in North Wales.

The biogas produced from the process is currently either burnt in the CHP engines or exported to the grid via the Five Fords WwTW Gas to Grid Facility (hereafter referred to as ‘the Facility’). Currently the Facility is operated under Permit number EPR/AP3139FT. The sludge treatment works and AD plant (hereafter referred to as ‘the Plant’) are currently outside the environmental permit area and are subject to a T21 exemption.

Since the existing sludge treatment digestion and sustainable energy plant became operational, new advanced anaerobic digestion (AAD) technologies have become well established. These technologies increase the yield of gas obtained from the digestion of sludge and result in a higher quality end product for use as fertiliser and are well suited for large scale centralised treatment of sludge.

It is now planned to install a Cambi thermal hydrolysis process (THP) plant, a form of AAD technology, at Five Fords WwTW, and for Five Fords to become a treatment centre for all sludge produced in North Wales, taking on additional satellite sites to those already importing liquid sludge into Five Fords. This will also allow the other digesters around north wales, many in a deteriorating condition, to be decommissioned.

The changes which will take place on site will mean that in future the AAD and sludge treatment facility will no longer meet the T21 exemption, and would, therefore, become a waste operation.

The AAD plant will be located immediately adjacent to the existing sludge treatment digestion plant, with modifications to the current AD process, and some minor modifications to equipment within the gas-to-grid permit area (removal of a boiler, modifications to the current combined heat and power (CHP) engines, and addition of another gas holder).

The proposed AAD plant will continue to process indigenous sludge from the Five Fords WwTW and will also receive a similar quantity of imported sludge. Additionally, Five Fords will start receiving cake (dewatered sludge) from several satellite sites for treatment, which will eventually make up 65% of the dried solids treated at the site. All sludge and cake will go through the new THP before being piped to the two current digester tanks, where biogas will be transported to the two gas holders. The produced gas will then be piped to the gas-to-grid installation (majority of the gas) or burnt in the two existing CHP engines to produce electricity. The current waste biogas burner will be retained and available to burn excess gas.

The proposed AAD plant will involve the following main changes:

Cake import facility to receive dewatered sludge from the satellite sites;

Cake silos for storage of cake prior to treatment in THPs;

Pre-THP dewatering facility for on-site sludge and liquid imports to allow for combined storage with imported cake in silos;

THP including two new boilers (1.567MWth each, with dual burners which can run on either biogas or natural gas) to provide steam to heat the THP streams. This is prior to the existing digestion facility;

One new additional gas holder;

Demolition of existing sludge buffer tanks prior to post digestion dewatering;

Re-use of existing pre-digestion sludge storage tanks for sludge storage upstream of the Pre-THP dewatering facility;

New post-digestion tank to the north of the cake export building;

Extensions and modification of the current cake export building to cater for increased production of cake;

Liquor Treatment Plant (LTP) to reduce pollutants in the post digestion dewatering centrate to acceptable levels before being pumped back to the WwTW;

Automated de-gritting system for existing digesters;

Removal of the current standby boiler (1.5MWth) located with the current CHP engines;

Modification of the current CHP’s (2.82MWth total), so that they no longer recover heat for the digesters.

The following are outputs from the process:

Cake (dewatered post digestion sludge) - stored in cake building before being shipped for use as a fertiliser;

Pre-THP centrate - pumped back to head of works for treatment;

Post-THP centrate - passed through the LTP to remove the majority of ammonia and is then pumped to the head of the works for treatment;

Bio gas - stored in gas holders, then passed through siloxane filters, then either:

Passed through the gas-to-grid plant before injection into grid;

Burnt in CHPs;

Used to run the THP boilers; and

Flared in the waste biogas burner.

Grit (small amount) – deposited in tip before taken off site.

Additional information

- The supporting document contains a description of the proposed changes, an assessment of the possible effects of this change and responses to all questions in the relevant forms - Parts A, C2, C3 and F1 - for the application documentation (plus supporting information where required). Completed forms A, C2, C3 and F1 are included within Appendix A.

- The Environmental Permit variation application document (‘the Main Supporting Document’) consists of two main parts:

Chapter 2 provides the general information required to inform Form C2 relating to the variation of a bespoke permit; and

Chapter 3 provides the more detailed information required to inform Form C3 relating to the variation of a bespoke installation permit.

- Form F1 covers Environmental Protection Operator and Pollution Risk Appraisal (EP OPRA) scores and the corresponding OPRA Spreadsheet is included electronically as Appendix B.

- Additional information included as part of this submission, are found in the following appendices:

Appendix A – Permit application forms

Appendix B – EP OPRA

Appendix C – Environmental Risk Assessment

Appendix D – Plans

Appendix E – Site Condition Report

Appendix F – Relevant Correspondence

Appendix G – Environmental Assessments

Appendix H – Schematics

# Introduction

## Overview

This document has been prepared to support the application to vary the existing bespoke Environmental Permit (hereafter referred to as ‘the Permit’) EPR/AP3139FT for the Facility on behalf of Dŵr Cymru Welsh Water (DCWW) (‘the Operator’). In order to satisfy the requirements of the Environmental Permitting Regulations (EPR) 2016, the Operator must apply to the Natural Resource Wales (NRW) for a change (variation) to an Existing Permit.

This document has been prepared to support an application to vary the Permit.

This is to account for the proposed changes at the wider Five Fords site, which include the addition of Advanced Anaerobic Digestion (AAD) to the current Anaerobic Digestion (AD) process which takes place at the site. As part of this change, the AAD and sludge treatment processes will require the importation of an increased amount of sludge and cake from other Wastewater Treatment Works (WwTW) satellite sites around North Wales, and will subsequently exceed its current T21 exemption (recover wastes at a wastewater treatment works), which allows the treatment of up to 100,000 cubic metres of waste over any 12-month period,  and covers the site.

This document contains a description of the proposed changes, an assessment of the possible effects of this change and responses to all questions in Parts A, C2, C3 and F1 of the application documentation (plus supporting information where required). Completed forms A, C2, C3 and F1 are included within Appendix A.

## Document content and structure

This environmental permit variation application document (‘the Main Supporting Document’) consists of two main parts:

Chapter 2 provides the general information required to inform Form C2 relating to the variation of a bespoke permit; and

Chapter 3 provides the more detailed information required to inform Form C3 relating to the variation of a bespoke installation permit.

Form F1 covers Environmental Protection Operator and Pollution Risk Appraisal (EP OPRA) scores and the corresponding OPRA Spreadsheet is included electronically as Appendix B.

- Additional information included as part of this submission, are found in the following appendices:

Appendix A – Permit application forms

Appendix B – EP OPRA

Appendix C – Environmental Risk Assessment

Appendix D – Plans

Appendix E – Site Condition Report

Appendix F – Relevant Correspondence

Appendix G – Environmental Assessments

Appendix H – Schematics

# General – Varying a bespoke permit (part C2)

## About the permit (Question 1)

The environmental permit that this application relates to is EPR/AP3139FT.

The address for the Plant is:

Five Fords WwTW Gas to Grid Facility

Cefn Road

Abenbury

Wrexham

Clwyd

LL13 0PA

## Existing Activities

DCWW is applying for a variation to account for changes to the current AD and sludge treatment centre which will exceed the T21 exemption (sometime in early 2019) and will, therefore, be classed as a waste operation. The variation will fall under the current gas-to-grid installation permit as a Directly Associated Waste Activity (DAWA).

A summary of the current permitted activities as part of the Facility is shown below:

Table 1: Permitted activities

| Table S1.1 Activities |  |  |  |
| --- | --- | --- | --- |
| Activity reference | Activities listed in Schedule 1 of the EP Regulations | Description of the specified activity | Limits of specified activity |
| A1 | Section 1.2 A (1) (a) – Refining gas where this is likely to involve the use of 1000 or more tonnes of gas in any 12-month period. | Refining of bio-gas produced from AD of Sewage Sludge prior to direct injection into National Gas Grid. | From receipt of raw bio-gas to entry to the National Grid including gas odorisation. |
| Directly Associated Activity |  |  |  |
| A2 | Propane Storage and Transfer Plant | Addition of propane to bio-methane to enhance calorific value of gas. | Storage and transfer of propane. |
|  | Description of activities for waste operations | Limits of activities |  |
| A3 | R1: Use principally as a fuel or other means to generate energy. | Treatment operations shall be limited to: 1. Burning of waste as a fuel for CHP production of hot water and electricity, from the receipt of raw materials to the despatch of products and waste. 2. Operation of a Waste Gas Burner (flare stack) from the receipt of biogas to the release of combustion products. 3. Storage of biogas arising from the AD process at Five Fords WwTW prior to combustion in the CHP engines and supplementary firing in the boilers or flaring. 4. Siloxane removal using a granular activated carbon filter, which will remove siloxane from the biogas deriving from the anaerobic digester prior to its combustion in the CHPs and the boiler. 5. Discharge of condensate from the gas pipelines and gas storage bag and from the siloxane removal media regeneration process, from collection to the point of discharge to the adjacent WwTW. |  |

Source:	Environmental Permit

### Existing Permitted Plant

The Facility, as currently permitted, allows for the upgrading and injection of biogas into the national gas grid. CHPs are also based on site which can combust biogas when needed. A dual fuel standby boiler is also retained on site, which can run on both natural gas and biogas, when needed.

The biogas produced from the existing sludge treatment and AD processes is currently outside of the environmental permit area.

The upgraded Plant will require the installation of new equipment, although a number of the existing assets will be reused as part of the enhanced digestion scheme. Some of these will require refurbishment. Table 2 lists the existing plant items within the current environmental permit.

Table 2: Existing plant items within the environmental permit EPR/AP3139FT (including any changes)

| Existing items in permitted boundary | Current Status | Capacity (where applicable) (m3 unless specified elsewhere) | To stay in place/reused/ replaced/removed as part of proposed changes |
| --- | --- | --- | --- |
| 1.5MW thermal output hot water boilers | Operational |  | Removed |
| Digester Heat Exchangers | Operational |  | Removed |

### Existing sludge treatment and anaerobic digestion

Sludge import and treatment and AD at Five Fords is currently regulated under a T21 exemption (Ref: NRW-WME009750) allowing the treatment of 100,000 cubic metres of waste brought to the works per annum.

The site imports sludge from other sewage treatment works in the area for treatment, in addition to treating the sludge produced by the on-site sewage treatment works. Imported sludge is brought in by tankers.

Indigenous and imported sludge and liquor from WwTWs in the region is accepted at the site and treated using AD. The waste is stored and blended before being pumped to the digesters. The digestion process breaks down the organic material in the feedstock, creating gases and digestate which forms a sludge cake on dewatering. The sludge cake is acceptable for use in agriculture. The resulting liquid returns to the digestion process or goes to the head of the WwTW.

The gas produced is passed to the Facility where it is refined and either injected into the national gas grid or burned in the two CHP engines (combined thermal input of 2.82MW).

## Changes to existing activities

### Changes to existing gas to grid facility (within current permit boundary)

No changes to the current Facility are anticipated.

The digesters, which are currently outside the gas-to-grid permit boundary, will be brought within the permitted site.  The updated permitted boundary is presented in drawing ref 4791-S-201-MMB-06-XX-DR-NX-06202-C03 in Appendix D.

### Changes to sludge treatment and anaerobic digestion (currently outside the permit boundary)

It is now planned to install a Cambi thermal hydrolysis process (THP) plant, a form of AAD technology, at Five Fords WwTW, and for Five Fords to become a treatment centre for all sludge produced in North Wales, taking on additional satellite sites to those already importing liquid sludge into Five Fords. This will also allow the other digesters around north Wales, many in a deteriorating condition, to be decommissioned.

The main changes to the sludge treatment activities to be included in the varied permit are summarised as follows:

Increased sludge treatment: the quantity of sludge treated at the site will increase to 104,465m3/annum.

Thermal Hydrolysis Plant (THP): a Cambi THP plant will be installed prior to the current digesters. This will increase the yield of gas obtained from the digestion of sludge and result in a higher quality end product for use as fertilizer. This will include two new boilers (1.567MWth each, with dual burners which can run on either biogas or natural gas) to provide steam to heat the THP streams.

Liquor Treatment Plant (LTP): a new LTP will be included within the new permit. This will reduce pollutants in the post digestion dewatering centrate to acceptable levels before being pumped back to the WwTW.

Details pertaining to the sludge and cake that will be imported into the Plant are displayed in Table 3. These figures are based on a worst-case scenario and were derived from Tables 3.10 and 4.2 of the Basis of Design Report (document ref DCWW-4791-S-201-MMB-06-XX-RP-CX-11001). The treatment capacity is 47tDS/day.

Table 3: Quantity of sludge and cake imported to the Plant

| Stream | Concentration (%DS) | tDS/year | Volume (m3/year) | Comment |
| --- | --- | --- | --- | --- |
| Imported – Existing LIQUID sludge imports | 3.8 | 1,500 | 39,420 | The concentration and delivery volumes are variable – especially the concentration. The concentration of 3.8%DS is based on measured values |
| Imported – proposed imported cake | 20 (minimum) | 13,009 (worst case including Queensferry – Phase 2 average) | 13009*100/20 = 65,045 | The % DS should be higher than this (i.e. volume lower) this value is used to be conservative. Also, density assume 1t/m3 which is also conservative. |
| Total | N/A | 14,509 | 104,465 | marginally over the 100,000 m3 “limit” |

- The proposed AAD plant will include the following changes:

Cake import facility to receive dewatered sludge from the satellite sites;

Cake silos for storage of cake prior to treatment in THPs;

Pre-THP dewatering facility for on-site sludge and liquid imports to allow for combined storage with imported cake in silos;

One new additional gas holder;

Demolition of existing sludge buffer tanks prior to post digestion dewatering;

Re-use of existing pre-digestion sludge storage tanks for sludge storage upstream of the Pre-THP dewatering facility;

New post-digestion tank to the north of the cake export building;

Extensions and modification of the current cake export building to cater for increased production of cake;

Automated de-gritting system for existing digesters;

Removal of the current standby boiler (1.5MWth) located with the current CHP engines; and

Modification of the current CHPs (2.82MWth total), so that they no longer recover heat for the digesters.

- The stages to the process in the LTP are as follows:

Only post-THP dewatering liquors are pumped to the LTP balance tank for buffering before being pumped forward for treatment.

The LTP feed pumps then pump the liquors to the LTP moving bed biofilm reactor (MBBR).

Before entering the reactor, the flow (warmed via the sludge coolers) passes through a static mixer where the low temperature final effluent is added to dilute and warm the liquors. Caustic soda is then dosed to add alkalinity to promote the conversion of ammonia into nitrogen gas.

Flow passes into the reactor, where it is mixed and treated utilising Anammox (anaerobic ammonia oxidation) technology. Air is added to the reactor using a blower and air distribution grid, and the flow is mixed using a paddle mixer, which keeps the media and ammonia oxidising bacteria in suspension.

Flow then passes forward to the LTP clarifier complete with half-bridge scraper. In this tank, effluent is wired over and discharged to the THP return pumping station where flow is discharged back to the main WwTW for further treatment. The sludge settled in the LTP clarifier is returned to the reactor as part of a returned activated sludge system.

When this sludge volume increases beyond a set volume, surplus activated sludge is diverted to the THP return pumping station and pumped to the main WwTW for settlement.

- Removal of:

Standby boiler

### Equipment to be installed

As already mentioned, the upgraded Facility will require the installation of new equipment. Table 4 shows the equipment to be installed as part of the new environmental permit boundary.

Table 4: Operational plant/ Equipment to be located within the new Environmental Permit Boundary

| Equipment | New item / Existing? | Storage capacity (where applicable) (m3 unless specified elsewhere) | Vents and values on storage tanks | Comment (where applicable) |
| --- | --- | --- | --- | --- |
| SAS buffer tank | Existing | XX | Odour controlled |  |
| Primary, SAS and Imports Gravity Belt Thickeners | Existing, Primary and Imports to be decommissioned, SAS to be retained | - | - | Located outside |
| Cake reception conveyors 1 & 2 | New | 2 x 30 | Odour controlled | Import area enclosed but not in building |
| Cake storage silos 1 & 2 | New | 2 x 300 | Odour controlled |  |
| Screened Sludge Holding Tank | Existing tank | XX | Odour controlled |  |
| Pre-THP Dewatering Feed Tank | Existing tank (Currently Digester Feed Tank) | XX | Odour controlled |  |
| Digesters (A & B) | Existing | 3,814 (each) | Pressure relief valves installed |  |
| Gas Holder complete with pressure relief valve | New | 1,350 |  |  |
| Post digestion tank coupled with air mixing/gas stripping system | New | 333 | Covered and odour controlled |  |
| Pre-THP Centrifuges 1 & 2 | 2 New | - |  | Within building |
| Pre-THP Polymer Dosing Plant | New | 12 |  | Within building |
| Strainpresses | 4 Existing and 1 New |  |  | Located outside |
| Liquid Import Rotamats | Existing |  |  | Located outside |
| Import area OCU | New | - |  |  |
| Post THP OCU | New | - |  |  |
| Liquid polymer dosing plant and storage tank | Existing |  |  | Located within a building for GBTs |
| Centrate PS | New | XX | Covered below ground manhole |  |
| Cake building | Upgraded Existing and New Extension | XX |  |  |
| THP Stream 1 & 2 coupled with compressors | New |  |  | 2No B4-3 Units |
| THP Sludge Coolers 1 & 2 | New |  |  | 3 stage cooler |
| Post THP Centrifuges 1, 2 & 3 | 3 New |  |  | Located within upgraded and repurposed north cake storage building |
| Post THP Polymer Dosing Plant | New |  |  | Located within upgraded and repurposed north cake storage building |
| Pre-THP Powder polymer storage silo | New | 15 tonnes | Covered with vent valve |  |
| Post-THP Powder polymer storage silo | Existing with screw conveyor upgraded | 15 tonnes | Covered with vent valve |  |
| LTP Balance tank | New | XX | Covered | AnitaTM Mox-HYBAS LTP |
| LTP Reactor tank | New | XX | Covered |  |
| LTP Clarifier | New | XX | Open topped with half bridge scrapper |  |
| LTP Blowers | New |  |  |  |
| Caustic Dosing Plant | New | XX | Covered and within bunded kiosk |  |
| Liquor PS | Existing | XX | Covered below ground manhole | Discharge location changed to be new THP Site Return PS |
| THP Site Return PS | New | XX | Covered below ground manhole | Discharge location upstream of ASP |
| Low Temperature Heated (LTH) FE Storage Tank | New | XX | Covered |  |
| High Temperature Heated (HTH) FE Storage Tank | New | XX | Covered |  |
| Softened Water Storage Tank | New | XX | Covered |  |
| Grit Dilution Tank | New | XX |  | Coupled with mixer |
| Auto-degrit system | New |  |  | Grit removal from digesters |
| Steam Boilers 1& 2 | New |  |  | Within a building |
| Steam Boiler Flue Stack | New | 15m |  |  |
| Potable water buffer tank | New | 20 | - | Located within upgraded and repurposed north cake storage building |
| Lime Dosing Plant | Existing |  |  | To be decommissioned |
| Lime Consolidation Tanks | Existing | XX |  | To be decommissioned |
| Limed Sludge Storage Tanks 1-4 | Existing | XX |  | To be removed |

Table 5 identifies the items of equipment that will be decommissioned as part of the upgrade works at Five Fords, and will, therefore, not be included in the permit.

Table 5: Items to be decommissioned and removed from the permit

| Equipment | New item / Existing? | Storage capacity (where applicable) (m3 unless specified elsewhere) | Vents and values on storage tanks | Comment (where applicable) |
| --- | --- | --- | --- | --- |
| Post digestion tank | Existing |  |  | Decommissioned |
| Lime Dosing Plant | Existing |  |  | To be decommissioned |
| Lime Consolidation Tanks | Existing | XX |  | To be decommissioned |
| Limed Sludge Storage Tanks 1-4 | Existing | XX |  | To be removed |

## Ability as an operator (Question 3)

### Relevant offences (3a)

Relevant offences since those listed in the application document for the initial environmental permit for the installation, are listed in Table 6.

Table 6: Relevant offences

| Conviction date | Court | Offence |
| --- | --- | --- |
| 11/12/2015 | Mold Magistrates | Environmental Permitting (England and Wales) Regulations 2010 |
| 04/11/2014 | Llandudno Magistrates | S.12 and S.38 Environmental Permitting (England and Wales) Regulations 2010 |
| 28/02/2014 | Wrexham Magistrates | S.12(1), and S.38(2) Environmental Permitting (England and Wales) Regulations 2010 |
| 12/12/2013 | Holyhead Magistrates | S.12(1)(b) and S38(1)(a) Environmental Permitting (England and Wales) Regulations 2010 |
| 20/11/2013 | Llandrindod Magistrates | 12(1), 38(1)(a) and 39(1) Environmental Permitting (England and Wales) Regulations 2010 |
| 19/11/2013 | Llandudno Magistrates | S.38(2) Environmental Permitting (England and Wales) Regulations 2010 |
| 18/11/2013 | Dolgellau Magistrates | S.12(1)(b), S38(2) and S.39(1)(a) Environmental Permitting (England and Wales) Regulations 2010 |
| 20/05/2013 | Haverfordwest Magistrates | 38(2) and 39(1) Environmental Permitting (England and Wales) Regulations 2010 |
| 05/04/2013 | Cardiff Magistrates | S.12(1), 38(1) and 29(1) Environmental Permitting (England and Wales) Regulations 2010 |
| 06/09/2011 | Hereford Magistrates | S.85(1) Water Resources Act 1991 |
| 21/04/2011 | Cardiff Crown | S.85(1) Water Resources Act 1991 |
| 11/04/2011 | Bridgend Magistrates | S.85(1) Water Resources Act 1991 and S.4(1) Salmon & Freshwater Fisheries Act 1975 |
| 24/06/2010 | Wrexham Magistrates | S.85(1) and S.85(6) Water Resources Act 1991 |
| 19/06/2009 | Llwynpia Magistrates | S.85(1) and S.85(6) Water Resources Act 1991 and S.4(1) Salmon & Freshwater Fisheries Act 1975 |
| 29/01/2009 | Wrexham Magistrates | S.85(6) Water Resources Act 1991 |
| 21/10/2008 | Abertillery Magistrates | S.85(1) and S.85(6) Water Resources Act 1991 and S.4(1) Salmon & Freshwater Fisheries Act 1975 |
| 18/09/2008 | Llwynpia Magistrates | S.85(1) and S.85(6) Water Resources Act 1991 and S.4(1) Salmon & Freshwater Fisheries Act 1975 |
| 24/07/2008 | Holyhead Magistrates | S.85(1) and S.85(6) Water Resources Act 1991 |
| 21/07/2008 | Mold Magistrates | S.85(6) Water Resources Act 1991 |
| 25/06/2008 | Stroud Magistrates | S.85(3) Water Resources Act 1991 |
| 11/01/2008 | Llwynpia Magistrates | S.85(6) Water Resources Act 1991 and S.4(1) Salmon & Freshwater Fisheries Act 1975 |
| 17/09/2007 | Aberdare Magistrates | S.85(1) and S.85(6) Water Resources Act 1991 and S.4(1) Salmon & Freshwater Fisheries Act 1975 |
| 17/09/2007 | Bridgend Magistrates | S.85(1) and S.85(6) Water Resources Act 1991 |
| 10/09/2007 | Aberdare Magistrates | S.85(1) and S.85(6) Water Resources Act 1991 and S.4(1) Salmon & Freshwater Fisheries Act 1975 |
| 26/07/2007 | Wrexham Magistrates | S.85(1) and S.85(6) Water Resources Act 1991 and S.4(1) Salmon & Freshwater Fisheries Act 1975 |
| 11/05/2007 | Ammanford Magistrates | S.85(1) and S.85(6) Water Resources Act 1991 |
| 14/03/2007 | Neath Magistrates | S.85(1) and S.85(6) Water Resources Act 1991 |
| 12/02/2007 | Bridgend Magistrates | S.85(1) Water Resources Act 1991 |

### Technical ability (3b)

All DCWW Wastewater Treatment Works Operators are put through rigorous training to ensure competence for the role. Initially all operatives will complete a Level 2 Wastewater Treatment Processes Programme which is 9-days’ duration and is delivered by Merit Skills. This consists of units from the Certification and Assessment Board for the Water Industry (CABWI) Diploma in Water Engineering with written assessments and covers all basic aspects of the wastewater process.

Six to twelve months later, the Operators will complete the Level 3 Competent Operator Programme. This is a 5-day training course followed by a 2-day one-to-one practical onsite assessment. The course is delivered by Water Training Solutions (a soletrader) and accredited by City & Guilds.

For operators with a role in the AAD process, DCWW has recently piloted training as part of the AAD harmonisation for Cardiff/Afan operators. This training course is called “Competent Operator for AAD” and additional units have been developed and added to the standard Level 3 programme described above. DCWW is seeking accreditation from City & Guilds for this course. The additional AAD specific units include:

| City & Guilds Boiler Operator Routines and Maintenance | Fulton | 1 day |
| --- | --- | --- |
| Knowledge of your Steam and Condensate System (manufacturer’s training) | Fulton | 1 day |
| Anaerobic Digestion Energy Management HACCP/BAS | Water Training Solutions | 2 days |
| Cambi THP | Cambi | 1 day |
| Radiation Protection Awareness | Public Health England | ½ day |
| Onsite practical assessment (one-to-one with assessor) | Water Training Solutions | 2 days |

An “Advanced Digestion – Technical Operator” Knowledge and Skills Framework has been developed to identify all the relevant training required for the role. Through monthly one to ones with line managers and the annual Performance Management Review Process, it is ensured that operations staff can demonstrate the knowledge and skills identified or are put forward for further training to develop the competency, if needed.

### Finances (3c)

No relevant persons, within Welsh Water, have current or past bankruptcy or insolvency proceedings against them.

### Management systems (3d)

#### Overview

DCWW has an Environmental Management System (EMS) Policy accredited to ISO14001 (see Appendix G).

In line with the EMS Policy, the Five Fords AAD and sludge treatment plant (STP) will be operated in accordance with the DCWW Quality Management System (QMS) EMS. The QMS was last audited in February 2017 and passed with no non-conformities.

DCWW has established and maintained documentation that defines and describes how the QMS is established, implemented and maintained in accordance with ISO 9001:2008 and ISO/IEC 17025:2005 and monitoring emissions to air, land and water (MCERTS) Standards.

The system is structured on the organisation’s strategic business areas, business processes and customer requirements.

DCWW has also established and maintained documentation that defines and describes how the EMS is established, implemented and maintained in accordance with ISO 14001:2004 for waste water operational sites. The EMS applies to all DCWW operations.

The EMS is not integrated with the QMS at present. However, certain system procedures and operating procedures are shared by both systems.  This is currently being updated by DCWW to include the THP facility.

Demonstrable procedures are outlined in the DCWW Environmental Policy Statement 2015 (see Appendix G) and the Site Operating Manual and QMS. DCWW have set out their long-term vision and direction in delivering its services in Welsh Water 2050.

An overall review of the QMS takes place every 12 months, and on other occasions, as required by Senior Management. There is a regular programme of audits covering all aspects of the QMS and EMS; they are included on the Internal Audit Programme operated by the Business Assurance team and audited by the Environment Agency (EA) on a frequent basis. In addition, the EMS and QMS are subject to audit by the inspection and certification company SGS (for accreditation purposes) every 6 months.

DCWW produces an annual report on environmental performance and, where required, attend local action group meetings.

The Biomethane Injection Plant (BIP) and THP will form part of the existing Facility and, as such, will be subject to the same management system arrangements.

One of the key tasks for DCWW during the permit determination process is the development of the management system arrangements for the AAD facility to cover the operations as well as the quality and environmental aspects.

#### Accident and Environmental Management Plan

Introduction

An Accident Management Plan, in the form of Environmental Emergency Procedures (Issue 05, 15th March 2015) and Site Emergency Plan (Version 2, October 2015), and Environmental Management Plan (Five Fords Waste Water Treatment Works – G2G Facility Environmental Management Plan, Issue 05, 22 November 2017) forms part of DCWW’s QMS.

An Accident Risk Assessment has been carried out for the installation, as has a Fire Risk Assessment (dated 19/06/2015) in accordance with the Regulatory Reform (Fire Safety) Order, 2005, these are implemented in accordance with the EMS requirements and is regularly reviewed.

In addition, an Environmental Risk Assessment (ERA) (see Section 2.6) has also been produced, in accordance with the EPR H1 guidance, and all risks identified by these assessments will be incorporated into the QMS.

One of the key tasks for DCWW during the permit determination process will be the incorporation of the arrangements for the new AAD and STP plant into the existing Management Plans for the permitted activities.

Assessment of risks

EPR Environmental Risk Assessment (ERA) for Permits guidance outlines that a risk assessment process should be undertaken following the identification of environmental hazards. The ERA has been updated to include the proposed changes to the Facility, and is provided in Appendix C.

Techniques to reduce risk

EPR guidance states that techniques should be implemented for the management and control of specific risks.

#### Complaints

All written complaints are covered by the Quality Manual QM(1) 01 and handled according to procedures (DG7 Process Reports). The implementation of the complaints procedure is detailed in CC(3) series procedures. Compliance with these procedures is part of the overall assessment of DCWW’s performance by OFWAT and there are penalties for poor performance. Telephone complaints are logged onto the DCWW SAP system and actions recorded by the DCWW operation and control centre (Linea). All complaints are analysed for root cause in order to prevent recurrence of the problem and assist with continuous improvement processes.

Complaints about pollution are dealt within the NO(03) 3 series procedures, and there are different procedures according to who reports the pollution. Pollutions may be reported via a number of routes including: general public, local authority, internally, contractor or formally via the Environment Agency. All pollution incident calls or emails are input into DCWWs online control system (SAP) by a Pollution Incident Advisor (PIA). This is then sent to the Waste Water Scheduling Team who allocates a Network Crew or contractor to respond to the incident; they have 4 hours to respond. After attending the incident, the operational crew provides feedback via SAP; the pollution incident details along with remedial actions taken or required are also verbally communicated to the Responsible Officer (RO). The SAP incident remains open until all follow-up work has been completed.

Following each incident, the relevant Pollution technician/Environmental Performance Officer reviews the findings and investigates details of the incident.  If the root cause of the incident is identified the appropriate remedial action is undertaken and the job is closed on SAP. If the root cause is not obvious, an enhanced investigation is instigated, and the findings reviewed for appropriate remedial action. Every category 1 and 2 pollution incidents are formally reviewed by the Head of Wastewater (Network).

## Supporting information (Question 5)

Plans provided, to satisfy question 5a, can be found in Appendix D.

The site condition report (SCR), produced for the Gas-to-Grid facility in 2014, is considered adequate for the permit variation as this sets the baseline against which future decommissioning will be compared.  A copy of the SCR can be found in Appendix E.

## Environmental Risk Assessment (Question 6)

### Introduction

As part of the application for an environmental permit, operators must assess the risk to the environment and human health from the activities that they propose to undertake. Using the methodology outlined in the EPR Guidance (H1), this section updates the original assessment of the risks to the environment and human health from the Five Fords Site that was submitted in relation to their original permit application for a gas-to-grid facility.  This variation application includes the addition of a THP plant and infrastructure included as a directly associated activity on the installation permit. A copy of the updated ERA (ref: DCWW-4791-S-201-MMB-06-XX-RP-NX-10310) can be found in Appendix C.

The ERA sets the requirements for the management of the permitted area, emission control measures etc. It assesses the additional risks, from the proposed THP processes, to the environment, amenity and human health. All control measures within the rules must be adhered to in order to obtain the permit.

Where emissions result in insignificant effects these have been screened out and where further detailed assessments of potential environmental impacts are required this is noted. A full description of the nature of the releases and measures to control them is provided in Section 3.2.

There is planning permission in place for these activities to be undertaken and the need for an environmental permit has come about through the changes made to the permitting legislation.

The ERA assesses the impacts from the following environmental concerns:

Point source and fugitive emissions to air;

Point source and fugitive emissions to water and land;

Noise and vibration;

Odour;

Litter;

Human and environment safety; and

Natural habitats and ecology.

### Impact Assessment

#### Overview

Five Fords WwTW is located at Ordnance Survey Grid Reference SJ 36054 48054. The WwTW is situated in a predominantly rural area with the surrounding areas consisting of agricultural land, within the village and parish of Marchwiel, approximately two kilometres to the south west of Wrexham.

The WwTW is immediately bordered by areas of woodland, arable and pastoral fields and their associated hedgerows. The River Clywedog is on the northern boundary of the WwTW and the town of Marchwiel is located just south of the WwTW.

- Information in this section is derived from desktop studies that have been undertaken for the Plant, and online resources such as:

Magic Interactive Map

#### Emissions to air

An air quality assessment (ref doc: DCWW-4791-S-201-MMB-06-XX-RP-NX-10311 – Five Fords AAD Air Quality Assessment, Nov 2018) has been undertaken to determine the effect on air quality associated with emissions from the site, relating to the installation of a THP facility.  The assessment was undertaken using advanced dispersion modelling.

For potential human health effects, the pollutant of key concern is NO2, although emissions of SO2 and CO have also been considered.  Effects of atmospheric concentrations of NOx and SO2 have also been assessed with respect to sensitive ecological sites.  The method of the assessment has taken a conservative approach by assuming worst case conditions for a number of aspects including emissions characteristics, operating scenarios and metrological conditions.

The results indicate compliance with all relevant environmental quality standards for both the protection of human health and designated sites. Overall impacts of all pollutants are considered to be insignificant and the proposed Plant is predicted to lead to an improvement in air quality compared to the existing configuration.

Abatement of other fugitive emissions to air

Based on the conclusions in the Air Quality Assessment no further abatement is required. However, best practice methods will be followed, during operation of the facility, to prevent the release of fugitive emissions.

#### Emissions to water and land

Water quality and resources

The water used at the Plant will be contained in a closed circuit; all wastewater streams will either be recycled within the process or captured and rerouted to the adjacent WwTW.

The AAD site will be covered in impermeable surfacing in order to contain any spillages and prevent mobilisation into the underlying groundwater. Site access roads will be built with kerbing to channel any surface spillages into the drainage network and prevent adjacent areas from being inundated. Any sewage spillages that occur will be limited in extent due to the site being secure with impermeable paving. There is sufficient capacity at the WwTW to handle the additional water input from the increased site area of the site.

Water use

There is one-point source release of wastewater from the BIP, which is discharged to the head of the on-site Five Fords WwTW (to sewer). This is limited to the small amounts of condensate present in the biogas feed to the BIP. The wastewater stream is directed to the WwTW drainage system and returned to the head of the works.

The majority of the process water, through the final effluent, will be diverted and further treated, through filtration and disinfection, for reuse within the THP.  Potable water, from the water network operated by Dee Valley Water, will be required for the boiler operation and polymer make up.

Point source emissions to surface waters, sewer and groundwater

The water used at the Plant will be contained in a closed circuit; all wastewater streams will either be recycled within the process or captured and rerouted to the adjacent WwTW.

Discharges will be minimal, typically arising from periodic maintenance/cleaning operations. As such, there are no direct potentially contaminated discharges to controlled surface waters and no significant impacts. All drainage (surface water or foul water) will be captured by the onsite drainage system and returned to the head of the WwTW.

The stormwater drainage of potentially contaminated areas from within the Plant boundary will be routed into the sewage treatment process with no discharge outside of the site. There will therefore be no risk of polluted runoff affecting off-site features due to the creation of a new hardstanding and plant area.

Flood risk

The site is located within the catchment of the Afon Clywedog and is within Flood Risk Zone A (as classified by the Environment Agency and NRW), considered to be at little or no risk of fluvial or tidal flooding from the Afon Clywedog.

The nearest ordinary watercourse is approximately 280m to the west of the WwTW and flows to the Afon Clywedog upstream of the site. It is considered that this watercourse does not present any risk to the site from flooding.

The drainage system within the AAD site directs all surface water back to the head (intake) of the works and on through the treatment process. Any increase in run-off will only affect flow through the WwTW and will not impact on neighbouring sites.

#### Odour

An odour assessment (document ref: MOMB16B_16_Final dated 16 July 2016) was undertaken to account for the upgrades to Five Fords WwTW, in order to assess the effect upon nearby receptors.

The key findings of the study were that the predicted change in odour emissions from sludge sources would be an increase of approximately 1%, however, despite this slight increase in odour emissions, the predicted offsite odour exposure levels for the proposed upgrade are predicted to reduce. This predicted reduction in offsite odour exposure is due to the change in the way odour emissions will be released, particularly in relation to the post-digestion centrifuges and cake handling and storage area, where emissions will be released at a height allowing for greater dilution and dispersion in the atmosphere.

The proposed upgrade is, therefore, not anticipated to increase the offsite impact or result in adverse impact upon nearby sensitive receptors or the amenity of the area surrounding the site.

Odour Control Units (OCUs) will be utilised in the cake import area and the cake export area to minimise odour emissions.

To date, the site has not received any odour complaints. This is confirmed in an email from DCWW, dated 7 November 2017, which is provided in Appendix F. The results of the odour assessment are shown in Appendix G.

#### Noise and vibration

The proposed changes to the Plant will use a combination of existing and new structures. No new equipment will be within 300m of any properties. A noise assessment (document ref: DCWW-4791-S-201-MMB-06-XX-RP-NX-19034, dated June 2016) was carried out as part of the planning application which demonstrated that noise from the proposed Plant will be below background noise levels at the nearest sensitive receptors. Therefore, potential impacts concerning noise are found to be insignificant. The noise assessment is provided in Appendix G.

A map identifying the nearest sensitive noise receptors can be found in Figure 1 and 2 of the noise assessment in Appendix G.

A maximum dB(A) figure, in accordance with DCWW specifications, is stated for all plant equipment being procured. Where this cannot be achieved, mitigation measures have been put in place to minimise noise to the local area and operators.

Since being operational, the current permitted activity has not received noise complaints to date. This is confirmed in the email from DCWW, dated 7 November 2017, which is provided in Appendix F.

The results of the noise assessment will need to be updated once the facility is operational to determine whether further mitigation needs to be incorporated.

#### Litter

Solid waste

Waste generated on the WwTW site includes the following:

| Waste Material | Recycled by: |
| --- | --- |
| Screenings/Grit | Wessex/Geneco |
| Scrap Metal | Alan’s Skip Hire |
| General/Paper | Alan’s Skip Hire |
| Waste Oils | Safety Kleen |
| Batteries | Alan’s Skip Hire |
| WEEE | Alan’s Skip Hire |
| Oil contaminated items | Safety Kleen |
| Aerosols | Alan’s Skip Hire |
| Gas cylinders | BOC |

To reduce volumes of waste:

All materials and consumables delivered to site are inspected to ensure that they are fit-for-purpose. Damaged items are refused and returned to the supplier.

Sewage sludge is de-watered from the works to be treated at the AAD Plant at Five Fords WwTW. Treated sludge is then recycled to agricultural land as a soil fertiliser. The treated sludge meets the Biosolids Assurance Scheme Quality Standards.  The volume of sludge recycled to agricultural land is monitored by the waste services team.

The Biomethane Gas from the sludge is processed in the gas-to-grid facility and injected back into the national Grid. Information on this can be found in the Gas to Grid Environmental Management Plan.

Polymer intermediate bulk containers (IBCs) are sent back to the supplier for re-use.

Grit is collected via an aggregates company and used as a soil conditioner. This process is licensed and controlled via the EA/NRW.

WEEE, batteries, waste oils and oil contaminated items such as oily rags are treated as hazardous waste in accordance with legislation, these are removed from site by an approved supplier procured through SRM Ltd, using the approved waste carriers in the DCWW Contract and Framework Directory.

Gas Cylinders for Nitrogen/Odorant/Calibration Gas etc. are collected by BOC Ltd from the Facility as they deliver a batch of new cylinders.

Five Fords WwTW has a designated waste management area that is located behind the offices next to the workshop. All skips and containers are located on a hardstand to prevent leaching into the ground. Skips and containers are clearly labelled. All waste from the Facility is sorted into this waste area at the main site other than the gas cylinders.

| Waste Carrier | Waste Carriers Registration Number | Waste Carriers License Expiry Date | Waste Removed |
| --- | --- | --- | --- |
| Safety-Kleen | CBDU89939 | 04/04/2019 | See Section 7. |
| Alan Skip Hire | CBDU3174 | 30/07/2018 | See Section 7. |
| BOC Ltd. | CBDU105757 | 01/05/2019 | See Section 7. |

#### Human health and environment safety

Visual impacts

The AAD Plant is screened from public views from the north, west and south by existing vegetation. The development will , however, be visible from a footpath to the east of the site. In order to limit the visual impact of the development from this viewpoint, the larger structures have, where possible, been located close to the existing digesters. In addition, tanks have been sited on an east to west alignment and in close proximity to existing structures so that the tank to the rear is partially screened. As part of the planning proposal, a screening bund will be provided along the eastern boundary of the proposed development. Visual impacts from the Plant are therefore considered to be low.

Site security

Activities are managed and operated in accordance with the management system. The site is categorised as a critical national infrastructure site by the Centre for the Protection of National Infrastructure (CPNI) and therefore, site security is paramount.  Access to site and waste is restricted by a 2.5m high chain link security fence and an automated pallisade gate (topped with barbed wire).  The site is manned 24 hours a day, 7 days a week.  Authorised personnel can gain access to the site using a fob system.  For visitors and unauthorised personnel an intercom system at the site entrance, is used.  The site also benefits from a CCTV systemsRegular inspections of the boundary fencing and buildings are undertaken to ensure that these have not been compromised and continue to prevent easy access to site.  Repairs are undertaken in accordance with the EMS requirements.

Other risks relating to human health and the environment is presented in the ERA in Appendix C.

#### Natural habitats and ecology

Sontley Marsh, a Site of Special Scientific Interest lies 2km to the west of the site and is the only statutory designated site within a 2km radius of the development.

Three non-statutory designated sites, Local Wildlife Sites (LWS), are located within 2km of the WwTW.  These are:

Marchwiel Marsh, located south, immediately adjacent to the WwTW

Cefn Park, located 1.5km North of the WwTW

Erddig Estate, located 1.7km to the west of the site

There are 26 Ancient Semi Natural Woodlands and Restored Ancient Woodlands within 2km of the WwTW, the closest of which are Marchwiel Covert, located within the WwTW boundaries and Black Wood, located within 100m north of the WwTW.

A Preliminary Ecological Appraisal (PEA) survey, undertaken as part of the Planning Application, found that the active site has low ecological value.

The proposed changes to the Plant will not affect sensitive receptors in proximity to the Plant. Impacts to sensitive receptors as a result of the Plant are as the findings of the original Environmental Permit Application and are considered to be minimal and adequately controlled.

Overall impacts are considered to be negligible.

# Part C3 – Variation to a bespoke installation permit

## Activities applying to vary (Question 1)

### Types of activity applied for

The proposed changes involve the modification of the existing STP, and upgrading of the current AD process to include a THP and LTP adjacent to the current AD site.  The upgraded works will become an AAD plant. The THP will be provided by steam produced from two new boilers.

The current standby boiler located next to the CHPs will be removed, as this will no longer be needed. The CHP engines will no longer provide heat to the digesters.

The types of activities that applyr are listed in Table 7.

Table 7: Types of activities

| Activity reference | Installation name | Schedule 1 references | Description of the activity | Activity capacity | Annex 2 (recovery) codes |
| --- | --- | --- | --- | --- | --- |
| A1 | Five Fords AAD Plant |  | Receipt of dewatered sludge at the cake import facility from the satellite sites. |  | R13 |
| A2 | Five Fords AAD Plant |  | Blending and storage of cake delivered from import facilities at cake silos prior to treatment in THP. |  | R13 |
| A3 | Five Fords AAD Plant |  | Dewatering of on-site sludge and liquid imports from pre-THP dewatering facility to allow for combined storage with imported cake in silos |  | R1 |
| A4 | Five Fords AAD Plant |  | Treatment of sludge using high pressure steam at the THP |  | R1 |
| A5 | Five Fords AAD Plant | Section 1.1 Part A(1) | Production of steam to heat the THP streams from two new boilers (1.567MWth each, with dual burners which can run on either biogas or natural gas). |  | R1 |
| A6 | Five Fords AAD Plant |  | Cooling of sludge and recycling of heat for use in the process. |  | R1 |
| A7 | Five Fords AAD Plant | Section 1.2 Part A(1) | Storage of biogas from digesters in two gas holders before further processing and a seal on the digesters is achieved. |  | R1 |
| A8 | Five Fords AAD Plant | Section 1.2 Part A(1) | Removal of impurities in the biogas at the siloxane removal plant. |  | R1 |
| A9 | Five Fords AAD Plant | Section 1.2 Part A(1) | Cleaning, upgrading and injection of biogas into the national grid after processing at the BIP. |  | R1 |
| A10 | Five Fords AAD Plant | Section 1.1 Part A(1) | Burning of gas at CHPs to turn it into electricity only when the biomethane plant is not online. |  | R1 |
| A11 | Five Fords AAD Plant | Section 1.2 Part A(1) | Stripping of the methane gas from the sludge in the post-digestion tank prior to further processing. |  | R1 |
| A12 | Five Fords AAD Plant |  | Processing and storage of treated sludge at the post-THP dewatering and cake storage building prior to being taken to land |  | R1 |
| A13 | Five Fords AAD Plant |  | Removal, separation, washing and storage of grit from the digesters at the de-gritting plant, prior to being exported as aggregated. |  | R1 |
| A14 | Five Fords AAD Plant |  | Further treatment of post digestion dewatering centrate from the post-THP dewatering process at the LTP to reduce pollutants in the liquid to acceptable levels prior to discharge to the main WwTW for further treatment |  | R1 |

### Types of waste accepted

The current T21 exemptions allows for the waste types, identified in Table 8, to be accepted.

Table 8: Types of waste accepted

| Waste Code | Description of Waste |
| --- | --- |
| 190801 | Screenings |
| 190802 | Sewage grit (waste from de-sanding) only |
| 190805 | Sludge from treating urban waste water |
| 190899 | Centrate liquor only |
| 190902 | Sludge from water clarification |
| 190903 | Sludge from decarbonation |
| 190906 | Solutions and sludge from regeneration of ion exchangers |
| 200304 | Septic tank sludge |
| 200306 | Waste from sewage cleaning |
| 200399 | Cesspool waste and other sewage sludge only |

Source:	UK Government – T21 Waste exemption. Accessed at https://www.gov.uk/guidance/waste-exemption-t21-recover-waste-at-a-waste-water-treatment-works#type-of-waste-you-can-treat

The only waste the Plant will be accepting is sludge from treating urban waste water (EWC 19 08 05). However, the list of waste types in Table 8 will be included as part of the permit as a contingency to the site operations.

Grit and screenings will be sent off-site to Geneco (Wessex Water) via Alans Skip Hire; cess pit and septic tank wastes will be delivered into the head of a works under Regulatory Position Statement 007 or Low Risk Position 378; while the other types of waste that can be treated as part of the T21 Exemption are not pertinent for the Plant.

## Emissions to air, land and water (Question 2)

### Introduction

This section identifies any point source emissions that are additional to those already identified in the current gas to grid installation permit.  It provides additional details relating to the emissions that result from the operating techniques described in Section 3.3.

### Point source emissions to air

An air quality assessment (ref doc: DCWW-4791-S-201-MMB-06-XX-RP-NX-10311 – Five Fords AAD Air Quality Assessment, Nov 2018) was undertaken to determine the effect on air quality associated with emissions from the site, relating to the installation of a THP facility.

The currently permitted point source emissions to air and the emission limit values (ELVs) for these  are summarised in Table 9.

Table 9: Emission limit values (ELVs) for Point source emissions to Air (as given in existing permit)

| Emission point and location | Parameter | Source | Limit | Unit | Reference period and Standard | Monitoring Frequency |
| --- | --- | --- | --- | --- | --- | --- |
| A1 CHP stack (1) | Oxides of Nitrogen (as NO2) | 1.41MW CHP engine exhaust stack | 500 | mg/m3 | Hourly average BS EN 14792 | Annual |
|  | Carbon Monoxide |  | 1400 | mg/m3 | Hourly Average BS EN 15058 | Annual |
|  | Total VOCs |  | 1000 | mg/m3 | Hourly Average BS EN 12619(4) BS EN 13526(5) | Annual |
| A2 CHP stack (2) | Oxides of Nitrogen (as NO2) | 1.41MW CHP engine exhaust stack | 500 | mg/m3 | Hourly average BS EN 14792 | Annual |
|  | Carbon Monoxide |  | 1400 | mg/m3 | Hourly Average BS EN 15058 | Annual |
|  | Total VOCs |  | 1000 | mg/m3 | Hourly Average BS EN 12619(4) BS EN 13526(5) | Annual |
| A3 Dual fuel standby boiler | Oxides of Nitrogen (NO and NO2 expressed as NO2) | 1.5 Dual fuel stand by boiler exhaust stack –operating on Biogas | 500 | mg/m3 | Hourly average BS EN 14792 | Annual |
|  | Carbon Monoxide |  | 1400 | mg/m3 | Hourly Average BS EN 15058 | Annual |
|  | Total VOCs |  | 1000 | mg/m3 | Hourly Average BS EN 12619(4) BS EN 13526(5) | Annual |
|  | Oxides of Nitrogen, and Carbon monoxide | 1.5 Dual fuel stand by boiler exhaust stack –operating on Natural gas | No limits set | - | - | Annual |
| A4 | Siloxanes | Siloxane removal unit | No limits set | - | - | - |
| A5 | Combustion gases | Waste gas burner (flare stack) | No limits set | - | - | - |
| A6 biomethane plant | Nitrogen Oxygen Carbon Dioxide Methane H2S Odour | Biomethane Plant Stack | No limits set | - | - | - |
| A9 | Biogas | Existing Gas Holder Pressure Relief Valve | No limits set | - | - | - |
| A10 | Biogas | New Gas Holder Pressure Relief Valve | No limits set | - | - | - |

Source:	Environmental permit EPR/AP3139FT

There are no point source emissions from the STP as part of normal operations. The only point source emission point to air as part of normal operations of the AAD process will be the emissions from the two new dual fuel boilers which supply heat and steam to the THP.

The proposed emission points for the variation application to permit are shown in (drawing 4791-S-201-MMB-06-XX-DR-NX-06202 C03 in Appendix D.

Table 10: Proposed emission points for variation to permit

| Emission point reference, and location | Source | Parameter | Amount | Unit |
| --- | --- | --- | --- | --- |
| A1 (current) | CHP stack 1 | NOx | 500 | mg/Nm3 |
|  |  | SO2 | - |  |
|  |  | CO | 1,400 |  |
| A2 (current) | CHP stack 2 | NOx | 500 | mg/Nm3 |
|  |  | SO2 | - |  |
|  |  | CO | 1,400 |  |
| A3 (will be removed) | Boiler stack - To be removed | To be removed | To be removed | To be removed |
| A4 (current) | Siloxane removal unit | Siloxane | No limits set | - |
| A5 (current) | Waste gas burner | Combustion gases | No limits set | - |
| A6 (current) | Biomethane Plant Stack | Nitrogen | No limits set | - |
|  |  | Oxygen |  |  |
|  |  | Carbon Dioxide |  |  |
|  |  | Methane |  |  |
|  |  | H2S |  |  |
|  |  | Odour |  |  |
| Gas Boiler 1 (to be added) | Biogas | NOx | 100 | mg/Nm3 |
|  |  | SO2 | 100 |  |
|  |  | CO | 12.5 |  |
| Gas Boiler 1 (to be added) | Natural gas | NOx | 100 | mg/Nm3 |
|  |  | SO2 | - |  |
|  |  | CO | 12.5 |  |
| Gas Boiler 2 (to be added) | Biogas | NOx | 100 | mg/Nm3 |
|  |  | SO2 | 100Error! Bookmark not defined. |  |
|  |  | CO | 12.5 |  |
| Gas Boiler 2 (to be added) | Natural gas | NOx | 100 | mg/Nm3 |
|  |  | SO2 | - |  |
|  |  | CO | 12.5 |  |

Source: Table 4: Stack emission parameters from the air quality assessment report - DCWW-4791-S-201-MMB-06-XX-RP-NX-10311 – Five Fords AAD Air Quality Assessment, Nov 2018

As part of the changes, the standby boiler currently in operation (emission point A3) will be removed, as it will be redundant.

The proposed new boilers will have one 14m high common stack, with one core per boiler. They will comprise 2 x 350mm diameter cores, with an actual stack diameter of 940mm. The thermal input will be 1.843MW, the boiler efficiency 85% and the steam output 2,500kg/hr.

A natural gas pilot will be operated on start up for both natural gas and biogas firing. Normal operation will depend on whether there is a signal for using biogas or natural gas. The exhaust gas exit temperature will be 150°C, while the emission limits are quoted as being 100mg/Nm3. The maximum hydrogen sulphide content of the biogas will be confirmed by the site.

The CHPs will remain but will only be used when the Facility is offline or for peak load lopping or TRIAD avoidance. The fuel of the CHPs will not change, but heat will be removed via the existing heat dump fan. Electricity produced will be utilised onsite. This change was implemented following the installation of the biomethane plan and should be minimal. Prior to the installation of the biomethane plant, the CHPs would have been in operation for most of the day; whereas going forwards, they are likely to be in operation for one day per month.

The calculations are based upon the air quality assessment (ref doc: DCWW-4791-S-201-MMB-06-XX-RP-NX-10311 – Five Fords AAD Air Quality Assessment, Nov 2018).

### Point source emissions to water

#### Point source emissions to water (other than sewers)

There will be no point source emissions from the THP. There are no direct potentially contaminated discharges to controlled surface waters, or direct discharge of wastewater to controlled waters from the THP.

There are also no direct potentially contaminated discharges to groundwaters.

Accidental releases of materials to the environment are controlled through adequate containment measures and working procedures.

#### Point source emissions to sewer, effluent treatment plant or other transfers off-site

There will be no point source emissions or direct discharges to controlled waters or public sewers, as part of the permit operation. Any liquid waste will either be reused or discharged to the drainage system of the adjacent Five Fords WwTW and will undergo treatment through the works before discharge to the River Dee. On-site WwTW effluent will meet the requirements of the existing discharge consent.

A list of the point source emissions to sewers, effluent treatment plants and other transfers off site is included as Table 11.

Table 11: Point source emission to sewers, effluent treatment plants or other transfers off site

| Emission point reference, and location | Source | Location | Grid reference | Characteristics |  | Monitoring / mitigation measures prior to final discharge and emission point discharge. |
| --- | --- | --- | --- | --- | --- | --- |
| W1 (existing and within the current permit) (discharged to Five Fords WwTW) | Condensate from the gas pipelines and gas storage bag | Adjacent to biogas storage | 340900, 347320 | - | - | - |
| W2 (existing and within the current permit) | Condensate from the siloxane removal media regeneration process | Adjacent to siloxane removal plant | 340900, 347320 | - | - | - |
| Boiler Water Treatment Plant | Water rejected by the Plant. |  |  | Will contain the same minerals found in potable water. | 2litres/day | Rerouted to adjacent WwTW |
| Boiler Maintenance | Boiler blow down to minimise damage from high mineral content water. |  |  | High purity water with traces of chemicals (used for boiler dosing). | Infrequent and negligible | Rerouted to adjacent WwTW. |
| Drain down of plant | Occurs during maintenance when it is necessary to drain down the feed water, hot well or boiler shell. |  |  | High purity water with traces of chemicals (used for boiler dosing). | Infrequent | Rerouted to adjacent WwTW. |
| Rainwater | Uncontaminated roof water from new buildings. |  |  | Clean rainwater from building roofs only. |  | Routed to water course via sealed system. |
| Rainwater | Run off from impervious surfaces |  |  | Clean rainwater from runoff |  | Rerouted to adjacent WwTW |
| Sanitary water | Domestic facilities. |  |  | Foul waste. | Negligible | Rerouted to adjacent WwTW. |
| Washwater | From the washing down of mechanical equipment during maintenance activities |  |  | Variable. | Negligible | Rerouted to adjacent WwTW. |
| Drain from foul gas skid | Cooling water from foul gas skid |  |  | Clean washwater | Negligible | Rerouted to adjacent WwTW. |
| Condensate | Gas pipelines and new gas storage bag |  |  | Condensate with slightly elevated levels of H2S dissolved from the biogas, resulting in a low level of acidity | Negligible | Rerouted to adjacent WwTW. |

Due to the anticipated very low levels of contamination of the water and the volumes involved, no monitoring of its composition is proposed prior to discharge to the WwTW, from the THP.

Any areas of the facility, where there is a risk of contamination of surface water, groundwater or discharge of process waters, are located on impermeable concrete surface.  All surface water from these areas drain to the WwTW internal drainage system and are returned to the head of the works for treatment prior to discharge as final effluent.

### Point source emissions to land

There will be no point source emissions to land as part of the activities carried out on site.

## Operating techniques (Question 3)

### Introduction

This section provides a technical overview of the components, the proposed techniques and measures to prevent and reduce waste arising and emissions of substances and heat, including during periods of start-up or shut-down, momentary stoppage and malfunction, and leaks.

Specifically, consideration is made of:

The technology to be used;

The process, in terms of how it will be operated and controlled;

In-process controls and Best Available Techniques (BAT) Assessment; and

Measures implemented to control emissions to air, water, sewer and land.

### Technical standards (Question 3a)

Table 12 lists the technical guidance notes (TGNs) used to inform the techniques and measures proposed to prevent and reduce waste arising and emissions of substances, including during periods of start up and shut down, momentary stoppage and malfunction, and leaks.

Table 12: Technical Standards

| Waste Activity, Schedule 1 activity or directly associated activity | Relevant Technical Guidance Note | Document reference (if appropriate) |
| --- | --- | --- |
| Burning any fuel in an appliance with a rated thermal input of 50 or more megawatts. | How to comply with your environmental permit Additional guidance for: Gasification, Liquefaction and Refining Installations (EPR 1.02) Best available techniques (BAT) conclusions, for common waste water and waste gas treatment/ management systems in the chemical sector | https://www.gov.uk/government/publications/gasification-liquefaction-and-refining-installations-additional-guidance http://eippcb.jrc.ec.europa.eu/reference/BREF/BATC_CWW.pdf |
| Refining gas where this is likely to involve the use of 1,000 or more tonnes of gas in any 12-month period. | How to comply with your environmental permit Additional guidance for: Gasification, Liquefaction and Refining Installations (EPR 1.02) Best available techniques (BAT) conclusions, for common waste water and waste gas treatment/ management systems in the chemical sector | https://www.gov.uk/government/publications/gasification-liquefaction-and-refining-installations-additional-guidance http://eippcb.jrc.ec.europa.eu/reference/BREF/BATC_CWW.pdf |
| General | - How to comply with your environmental permit - EA/NRW’s horizontal environmental permitting guidance, including: H1 Software tool and guidance H2 Energy efficiency H3 Noise assessment and control H4 Odour management H5 Site condition report | https://naturalresources.wales/permits-and-permissions/environmental-permits/guidance-to-help-you-comply-with-your-environmental-permit/?lang=en https://naturalresources.wales/permits-and-permissions/environmental-permits/horizontal-guidance/?lang=en |

A copy of the schematics describing the operation and process can be found in Appendix H.

### General requirements (Question 3b)

#### Overview

This section provides an overview of the measures in place at the Plant for controlling fugitive emissions, noise and odour. An ERA has been completed, in accordance with the H1 ERA Guidance, and is provided in Appendix C.

#### Control of fugitive emissions to air

There are no significant fugitive emissions to air of gases, vapours, or particulates as part of normal operation or in resepct to the proposed changes.

#### Control of fugitive emissions to surface water, sewer and groundwater

There is appropriate containment for the control of liquid wastes put in place to minimise any potential releases, as identified in the EMS

#### Odour

As discussed in Section 2.6.2.6, odour is controlled via one current OCU and two proposed additional OCUs to account for the changes on site.

The current site has, to date, not received any odour complaints during its operation.

The predicted change in odour emissions from sludge sources is expected to lead to an increase of approximately 1%, however, despite this slight increase in odour emissions, the predicted offsite odour exposure levels for the proposed upgrade are predicted to reduce. This predicted reduction in offsite odour exposure is due to the change in the way odour emissions will be released, particularly in relation to the post-digestion centrifuges and cake handling and storage area, where emissions will be released at a height allowing for greater dilution and dispersion in the atmosphere.

The proposed upgrade is therefore not anticipated to increase the offsite impact or result in adverse impact upon nearby sensitive receptors or the amenity of the area surrounding the site.

#### Noise

The current permitted activity has not received any noise complaints to date as identified in Section 2.6.2.5.

The additional Plant will continue to operate in accordance with the noise conditions stated in the current Environmental Permit. Following the EPR H1 methodology, it has been determined that appropriate noise control measures are in place.

### Type and amounts of raw materials (Question 3c)

All raw materials that will be used at the AAD plant are identified in Table 13. This list will be maintained and updated throughout the lifetime of the permit and updated within the Site Operating Manual.

Table 13: Types and amount of raw materials

| Description of raw materials and composition | Maximum amount (tonnes) | Annual throughput (m3 unless specified) | Description of how the raw material is used including any main hazardous (inc. MSDS) |
| --- | --- | --- | --- |
| Biogas (~63% Methane, 35% Carbon Dioxide, 2% Oxygen/ Nitrogen) | Direct feed | 7254 | Feed gas for biomethane enhancement. Fire/explosion asphyxiation |
| Propane (C3H8) | 15 | 349 | Propane enrichment of biogas. Fire/explosion. |
| Gas odorant (Mercaptans) | 0.025 | 0.12tpa | Legal requirement to add odour to gas stream. Flammable, irritant |
| Carbon Filters | 8 (4No. 2 tonnes filters) | 9-17No. (1-2 replacement cycles per year) | Off gas cleaning/ carbon filtration. Carbon dust – respirable hazard/irritant |
| Polymer | 30 | 201tpa | Improves dewatering of sludges. Can create a slip hazard if spilled. Stored in bunded units. |
| Lube oils | 0.2 | 0.4tpa | Lubricant |

### Information for specific sectors (if needed) (Question 3d)

The activity does not fall under the Medium Combustion Plant Directive (EU2015/2193) because the heat generated by the plant is used to produce steam and is not used directly for any biological treatment such as anaerobic digestion; therefore, Appendix 1 of Form C3 is not required.

Additionally, as the BAT Conclusions, have been completed, the requirement to complete Appendix 5 of Form C3 is not considered necessary.

### Monitoring (Question 4)

This section provides a summary of the proposed monitoring of the Plant.

#### Monitoring of emissions to air

Welsh Water has monitored Volatile Organic Carbon (VOC) emissions arising from the Combined Heat and Power engines at Five Fords WwTW since commissioning in 2012. As part of this permit variation, DCWW propose that the requirement for annual monitoring of VOC  emissions along with the 1,000mg/m3 threshold currently stipulated, is removed from the permit.

An H1 Environmental Assessment submitted to NRW, in 2016 using worst-case data, showed that even though the site does not meet the VOC Emission Limit Value (ELV) required in the Environmental  Permit, there is no environmental degradation or impact caused, by this exceedance.   This has been agreed with NRW’s Regulatory Officer and Appendix F provides supporting evidence of this.

Subsequent discussions with NRW’s Combined Heat and Power expert, agreed Welsh Water had robust maintenance and condition analysis in place through their maintenance provider, Edina. It is, therefore, proposed that the permit variation removes the requirement for VOC emissions testing and any threshold stipulated. To facilitate this, Welsh Water will continue to maintain the assets to their current standard and continue with weekly oil analysis, trending and condition monitoring processes to ensure the plant operates as efficiently as possible, in line with environmental requirements.

In addition to this, Welsh Water submits Combined Heat and Power engine efficiency data to Ricardo AEA as part of the ‘Good Quality CHP’ scheme, in March, for the previous Calendar Year. Welsh Water also submits Calendar Year efficiency data to NRW the following March. It would be an administrative improvement to amend the Calendar Year environmental performance submission for Five Fords WwTW to March to align with other reporting deadlines. Welsh Water, therefore, ask this amendment is also made as part of the variation.

No abatement technology is required and continuous monitoring is not considered necessary.

#### Monitoring and reporting of emissions to water and sewer

There are no direct releases to controlled waters or public sewers of emissions arising from the Plant. As such, no monitoring or reporting for the additional Plant is required.

#### Monitoring of waste emissions

As required by the DCWW EMS, various housekeeping and waste management practices are in place. These include segregation of wastes according to their classification and nature, labelling waste and using designated storage containers.

In accordance with the DCWW EMS Policy WO(3) 01, solid waste is disposed of in accordance with ‘Duty of Care’ Regulations. The composition of the waste, its hazard characteristics and any relevant precautions is clearly stated on the transfer notes provided to licensed waste contractors removing waste from site for recycling and/or disposal. Records are maintained on site and reported to the regulator as required by the EPR permit.

### Resource efficiency and climate change (Question 6)

#### Basic measures for improving energy efficiency (Question 6a)

Biomethane is a renewable gas, produced from organic waste and injected into the gas grid.  Biomethane can make a contribution to the UK’s low carbon economy, will help to manage organic waste products and has the added benefit of being a secure energy supply.

The benefit of biomethane as a renewable gas is recognised through the UK Government’s Renewable Heat Incentive (RHI) scheme which provides financial incentives to promote the generation of renewable heat and biomethane. The gas to grid plant has been accredited with the ISCC to attribute a carbon footprint to the renewable gas, in conjunction with the schemes registration into the new ‘Green Gas Certification Scheme’ administered by Renewable Energy Assurance Ltd. This gives additional assurances of the sustainability of the renewable gas produced.

Basic Energy Requirements

The design will maximise the efficiency of the energy flows from the process ensuring that, where possible, excess process heat from one stage is recovered to feed other stages which require a heat input.  This will be carried out using heat exchangers to transfer process heat.

There are a number of pieces of equipment that will need an electrical energy supply including:

Fans / coolers;

Pumps / boosters/conveyors;

Thermal Hydrolysis Plant;

Sludge dewatering and polymer dosing equipment;

Compressors, and;

Gas driers.

Current design information suggests that at 300Nm3/hr biogas throughput, the process will require an annual energy input of 750 MWh/yr.  There is no use of fuel oils or natural gas on the biogas upgrade plant (BUP) but natural gas will be used for the steam raising boiler(s).

Energy Efficiency measures

A key objective of the DCWW EMS is to reduce energy consumption from the grid. Procedure EMP 003 specifically contains objectives for the Reduction of Energy Consumption Programme; this includes the commitment to produce monthly usage energy reports that are to be sent to Senior and Operational management and obtaining detailed electricity usage information via metering of specific areas of plant.

Energy efficiency measures implemented at the current plant include the following:

When in operation, the combustion temperature is maintained relatively constant for reduced NOx emissions and increased efficiency.

Heat from the sludge cooling, following the thermal hydrolysis plant, is recovered and then used in the process of the AAD plant by pre-warming the boiler water and sludge, reducing gas consumption.

When in operation, the engines are equipped with turbochargers, further increasing energy efficiency.

Ongoing monitoring of plant operating parameters is carried out to ensure process is operating optimally and to enable constant optimisation to increase the plant’s efficiency.

The maintenance scheme in place ensures fuel is combusted as completely as possible and heat is transferred efficiently.

Good housekeeping measures are employed, and regular preventative maintenance will ensure the operations, and therefore energy efficiency, is optimised.

Low cost measures in place to avoid inefficiencies of excessive heating or cooling, include:

Insulation of main hot water pipes; and

Insulation of heating equipment such as steam raising boiler feed, sludge coolers and boiler feed water pumps and pipework.

These measures will also be implemented once the AAD plant is in operation.

The CHP area is not located in a building but housed in acoustic containers. The only building associated with the original planning application was the heating plant room housing the Low Temperature Hot Water (LTHW) circulation pumps and boiler feed water treatment. There are limited opportunities for energy efficiency requirements as the buildings are not heated. Energy efficient lighting will be used throughout the building.

The steam raising boilers are located within a building which protects the plant for excessive heat loss. The planning application covered the entire AAD development.

As part of the OFGEM and Combined Heat and Power Quality Assurance (CHPQA) Programme requirements, usable heat will be measured and reported on a monthly basis. The monitoring scheme monitors gas use against energy production to determine performance. To achieve government incentives DCWW also monitors heat recovered, electricity production, gas use and overall efficiency of the installation. This information can be used to generate a database for further determination of energy efficiency plans.

An energy efficiency plan will be developed once the site is operational; this will determine areas of improvement and will be developed under DCWW’s Environmental Policy and EMS.

#### Breakdown of any changes to the energy the activities use and create (Question 6b)

Following the completion of the AAD plant, biogas will continue to be upgraded and injected into the national gas grid. However, the total biogas flow will increase due to an increase in the percentage conversion of organic matter into gas due to thermal hydrolysis. This process makes the existing assets more efficient.

The thermal hydrolysis process requires high pressure steam, which is created using a new steam raising boiler and utilises natural gas in normal operation. This boiler does also have the facility to use biogas should it be available, for example, during BUP maintenance periods.

The CHPs will continue to operate, but only periodically to help the WwTW optimise its onsite power usage, specifically electricity. In normal operation, biogas will be upgraded and injected into the grid.

#### Climate change (Question 6c)

DCWW is not a participant to the Climate Change Levy Agreement.

#### Specific measures for improving energy efficiency (Question 6c)

The thermal hydrolysis process requires steam at a high pressure. To generate this steam, natural gas is used. To improve the energy efficiency of the plant, a three-stage heat recovery system is put in place. The first stage is a potable water circuit which recovers high grade heat to heat the boiler hot well. The second stage is medium grade and uses a final effluent loop to pre-warm the sludge pre-thermal hydrolysis to reduce steam demand. The final stage is low grade heat, which uses the final effluent to pre-warm the polymer used in sludge dewatering, again warming the sludge.

The heat recovery system ensures the energy used is utilised as efficiently as possible in the plant.

#### Efficient use of raw materials and water (Question 6d)

All materials will be handled and stored in such a way are to ensure containment. Fugitive emissions to the environment are therefore negligible.

Biogas is the primary raw material. Its consumption will be continuously monitored. The use of biogas as the fuel source offers the best environmental option and there is therefore no environmental incentive to reduce biogas consumption and consider an alternative source of fuel.

Biogas is stored within 2No. double membrane inflatable bag type holders, constructed of PVC coated polyester fabric, which is resistant to UV and microbial degradation. The base of the holders are constructed from reinforced concrete treated to withstand the potentially acidic conditions within the holder. The gas bag is completely enclosed so the gas is not in contact with the concrete.

Secondary raw materials include chemicals used in processes such as water treatment, polymer and natural gas for the steam raising boiler. Their consumption will be monitored, based on purchase records. No water is used in the BIP.

Natural gas is required to run the burners in the steam raising boiler house. This steam is required for the thermal hydrolysis process.  Natural gas is not stored on site, but taken direct from the mains supply.

Water treatment chemicals are stored within the boiler building in tablet form on hard standing and within a contained drainage area. Polymer is stored in sealed silos located on bunded areas.

The DCWW purchasing procedures are included in DCWW QMS PP(3) series. The procedures ensure purchased items conform to specified requirements, including quality parameters, and review suitability for use, including efficiency and minimisation of use of raw materials.

All substances are assessed for COSHH (Control of Substances Hazardous to Health) compliance, where relevant. Material safety data sheets for all materials used and kept on site will be maintained on the site.

All raw materials are handled and stored within the confines of the buildings on site, or silos following the unloading from vehicles, with the exception of biogas which is contained within the gas handling system.

Releases of raw materials to land are considered to be negligible due to adequate containment of the materials within suitable storage vessels and presence of a contained drainage system.

#### Avoidance, recovery and disposal of wastes (Question 6e)

The proposed AAD plant at Five Fords will manage its waste streams in accordance with the Council Directive 2008/98/EC on waste (the Waste Framework Directive), ISO 14001, legal requirements and DCWW EMSs. There will be a Waste Management Plan that includes details of the types of waste produced at site, how wastes are segregated, stored and removed from site. Only minimal volumes of waste shall be generated at the AAD plant, with waste streams segregated and recovered for recycling where possible. All waste streams shall be managed in accordance with existing EMSs, with any final off-site disposal to be carried out by licensed waste contractors in accordance with Duty of Care requirements.

Implementation of EMS procedures and the current Environmental Policy ensures optimum disposal of the wastes produced. Submission of a detailed assessment is not considered necessary due to the minimal quantity of waste produced.

Further consultation with waste contractors will ensure that all waste streams have been considered. The sampling and characterisation of wastes will be covered under the requirements of Duty of Care.

The wastes will be stored in suitable designed containers prior to being removed from site.

Disposal routes for the waste streams have still to be determined, but the application of the waste hierarchy will be central to the decision making process.

# Part F1 – OPRA, charges and declarations

## Working out charges (Question 1)

Table 1 of the F1 form has been completed.  An up-to-date EP OPRA profile is provided in Appendix B.

## Payment (Questions 3)

Payment will be by BACS

## Confidentiality and National Security (Question 5)

DCWW wish to claim confidentiality of some of the information provided in the application.  This is on the basis of national security and public safety.  Justification for this claim, along with a list of confidential documents, has been provided separately in the letter dated 5 July 2018 from DCWW’s Security Manager, as part of the covering letter for the application.

## Application Checklist (Question 6)

Table 14 provides a list of documents included in the application

Table 14: Application Checklist

| Question reference | Document title/reference | Document section |
| --- | --- | --- |
| Part C2 – Q2b | Non-Technical Summary | Main Supporting Document |
| Part C2 – Q3a | List of Relevant Offences | Section 2.4.1 of Main Supporting Document |
| Part C2 – Q3d3 | Environmental Management System summary | Section 2.4.4 of Main Supporting Document |
| Part C2 – Q5a | Site Plans | Appendix D of Main Supporting Document |
| Part C2 – Q5b | Site Condition Report | Appendix E of Main Supporting Document |
| Part C2 – Q6 | Environmental Risk Assessment | Appendix C of Main Supporting Document |
| Part C3 - Q1a | Listed Activities | Section 3.1, Table 7 of Main Supporting Document |
| Part C3 – Q1b | Waste Codes | Section 3.1, The current T21 exemptions allows for the waste types, identified in Table 8, to be accepted. Table 8 Main Supporting Document |
| Part C3 - Q2 | Emissions to air, land and water | Section 3.2, Table 9, Table 10 and Table 11 of Main Supporting Document |
| Part C3 – Q3a | Technical Standards | Section 3.3, Table 12 of Main Supporting Document |
| Part C3 – Q3a | Schematics | Appendix H of Main Supporting Information |
| Part C3 – Q3b | General requirements | Section 3.3.3 of Main Supporting Document |
| Part C3 – Q3c | Types and amounts of raw materials | Section 3.3.4, Table 13 of Main Supporting Document |
| Part C3 - Q3d | Information for specific sectors | See Section 3.3.5 of main supporting document |
| Part C3 – Q4a | Monitoring | Section 3.3.6 of Main Supporting Document |
| Part C3 – Q4b | Point Source emissions to air | Section 3.3.6.1 of Main Supporting Document |
| Part C3 – Q6a | Basic measures for improving energy efficiency | Section 3.3.7.1 of Main Supporting Document |
| Part C3 – Q6b | Breakdown of any changes to the energy the activities use and create | Section 3.3.7.2 of Main Supporting Document |
| Part C3 – Q6c | Climate Change Levy Agreement | Sections 3.3.7.3 and 3.3.7.4 of Main Supporting Document |
| Part C3 – Q6d | Raw and other materials, substances and water use | Section 3.3.7.5 of Main Supporting Document |
| Part C3 – Q6e | Waste Avoidance | Section 3.3.7.6 of Main Supporting Document |
| Part F1 – Q5 | Five Fords signed disclosure letter | Section 4.3 of Main Supporting Document |
| Part F1 – Q6 | Application Checklist | Section 4.4 of Main Supporting Document |

Appendices

A. Permit Application forms 42 B. EP OPRA 44 C. Environmental Risk Assessment 46 D. Site Plans 48 E. Site Condition Report 52 F. Correspondence 54 G. Environmental Assessments 56 H. Schematics 58

Permit Application forms

EP OPRA

Environmental Risk Assessment

Site Plans

Site Location with Permitted Boundary

Site Boundary and Emission Points

Site Condition Report

Correspondence

Environmental Assessments

Schematics

mottmac.com

Dŵr Cymru Welsh Water, March 2018 – Welsh Water 2050. Available online at https://www.welshwater.com/en/Company-Information/Business-Planning/Welsh-Water-2050.aspx

http://magic.gov.uk/MagicMap.aspx

Regulatory Position Statement 007 – The disposal of septic tank and cesspool sludge from domestic dwellings and arisings from blocked sewers.

Low Risk Position 378 – The treatment of a maximum of 100,000m3 in any 12-month period of septic tank liquor at sewage treatment works other than at the site where the septic tank sludge is dewatered.

Normalised conditions = 3% O2, 273.15 K, dry, 1 atm

The expected H2S content of biogas is 46ppm and therefore concentrations in flue gas will be significantly below 100mg/Nm3 limit assumed in the assessment.

(Commission Implementing Decision (EU) 2018/1147 of 10 August 2018 establishing best available techniques (BAT) conclusions for waste treatment, under Directive 2010/75/EU of the European Parliament and of the Council (notified under document C(2018) 5070)).

International Sustainability & Carbon Certification - https://www.iscc-system.org/