[image: image2.png]Environment
W Agency




Permit with introductory note

The Environmental Permitting (England & Wales) Regulations 2010
Dŵr Cymru Cyfyngedig 
Afan Combined Heat and Power Facility 
Afan Waste Water Treatment Works Harbour Road

Phoenix Walk
Port Talbot Steelworks

Port Talbot

SA13 1RA
Permit number

EPR/ZP3032KQ
Afan Combined Heat and Power Facility
Permit Number EPR/ZP3032KQ
Introductory note

This introductory note does not form a part of the permit

The main features of the facility are as follows.
The installation is located within Afan Waste Water Treatment Works (WwTW), and covers an area of approximately 0.25ha. The centre of the installation is located at National Grid Reference SS 7612 8732. 

The installation is bounded to the north and east by Port Talbot Steelworks with Margam Sands and Swansea Bay to the south and west. The nearest residential properties are approximately 1.8 km away being Margam to the north east and Aberafan to the north. Margam Moors SSSI and Eglwys Nunydd Reservoir SSSI lie approximately 2.9 km and 3.4 km to the south east respectively

Biogas will be generated during an Advanced Digestion process at the WwTW which will be captured and stored in two dual membrane gas storage bags, (2,000 m3 storage capacity each, predicted to be equivalent to 3.2 hours of production from the digesters). The biogas will then be transferred to the Combined Heat and Power (CHP) engines where it will be combusted in two spark ignition engines with a rated thermal input of 3.745 MW each, (1.56 MWe output each). 

The CHP engines will be used to generate electricity via an alternator and heat via the engine exhaust and cooling jacket. The electricity will be utilised within the WwTW with any surplus being transferred to the distribution network.

High grade heat will be recovered from the CHP engine exhaust and used to generate low pressure steam, whilst the low grade heat from the cooling jacket will be used to generate hot water for re-use in the Advanced Digestion process. Additional heat demand will be met by two supplementary fired waste heat boilers, (3.9 MWth input each). The fuel used for supplementary firing will ordinarily be natural gas, but under certain circumstances (such as a CHP engine being unavailable) will be biogas.
A gas flare will be provided capable of burning biogas at a flow rate of 2,000 Nm3/hr, (compared to a predicted biogas production rate of 790 Nm3/hr).  

Potential impacts from the installation arise from the emission of combustion products to air. 

There are no significant emissions of noise or odour predicted and the activities will not give rise to any significant releases to land, water or sewer, (boiler blowdown, condensate and surface water run off are returned to the site drainage system, which leads to the head of the WwTW).  

Flood risk has been addressed by developing the site infrastructure at a height above the maximum 1 in 1000 return period tide levels.  

The status log of the permit sets out the permitting history, including any changes to the permit reference number 
	Status Log of the permit

	Detail
	Date
	Comments

	Application EPR/ZP3032KQ/A001
	Duly made 27/11/09
	

	Permit determined
	DD/MM/YY
	


End of Introductory Note

	Permit


The Environmental Permitting (England and Wales) Regulations 2010
Permit
Permit number 

EPR/ZP3032KQ
The Environment Agency hereby authorises, under regulation 13 of the Environmental Permitting (England and Wales) Regulations 2010 
Dŵr Cymru Cyfyngedig, (“the operator”),

whose registered office is

Pentwyn Road

Nelson

Treharris

Mid Glamorgan 

CF46 6LY

company registration number 2366777 
to operate an installation at

Afan Combined Heat and Power Facility 

Afan Waste Water Treatment Works 
Harbour Road

Phoenix Walk
Port Talbot Steelworks

Port Talbot

SA13 1RA

to the extent authorised by and subject to the conditions of this permit.

	Name
	Date

	
	26/05/10


Avril Varley-Brown

Authorised on behalf of the Environment Agency

Conditions 
1 Management
1.1 General management

1.1.1 The operator shall manage and operate the activities:

(a) in accordance with a written management system that identifies and minimises risks of pollution, including those arising from operations, maintenance, accidents, incidents, non-conformances, closure and those drawn to the attention of the operator as a result of complaints; and
(b) using sufficient competent persons and resources.

1.1.2  Records demonstrating compliance with condition 1.1.1 shall be maintained. 

1.1.3 Any person having duties that are or may be affected by the matters set out in this permit shall have convenient access to a copy of it kept at or near the place where those duties are carried out.

1.2
Energy efficiency

1.2.1
The operator shall:

(a)
take appropriate measures to ensure that energy is used efficiently in the activities;

(b)
review and record at least every four years whether there are suitable opportunities to improve the energy efficiency of the activities; and  

(c)
take any further appropriate measures identified by a review. 

1.3
Efficient use of raw materials

1.3.1
The operator shall:

(a)
take appropriate measures to ensure that raw materials and water are used efficiently in the activities; 

(b)
maintain records of raw materials and water used in the activities;

(c)
review and record at least every four years whether there are suitable alternative materials that could reduce environmental impact or opportunities to improve the efficiency of raw material and water use; and

(d)
take any further appropriate measures identified by a review.

1.4
Avoidance, recovery and disposal of wastes produced by the activities

1.4.1
The operator shall:

(a)
take appropriate measures to ensure that waste produced by the activities is avoided or reduced, or where waste is produced it is recovered wherever practicable or otherwise disposed of in a manner which minimises its impact on the environment;

(b)
review and record at least every four years whether changes to those measures should be made; and 

(c)
take any further appropriate measures identified by a review.
2
Operations
2.1
Permitted activities

2.1.1
The operator is only authorised to carry out the activities specified in schedule 1 table S1.1 (the “activities”). 

2.2
The site 

2.2.1
The activities shall not extend beyond the site, being the land shown edged in green on the site plan at schedule 7 to this permit.

2.3
Operating techniques

2.3.1
(a) 
The activities shall, subject to the conditions of this permit, be operated using the 


techniques and in the manner described in the documentation specified in 
schedule 1, table S1.2, unless otherwise agreed in writing by the Environment 

Agency.

(b)
If notified by the Environment Agency that the activities are giving rise to pollution, the operator shall submit to the Environment Agency for approval within the period specified, a revision of any plan specified in schedule 1, table S1.2 or otherwise required under this permit, and shall implement the approved revised plan in place of the original from the date of approval, unless otherwise agreed in writing by the Environment Agency.
2.3.2
The operator shall ensure that where waste produced by the activities is sent to a relevant waste operation, that operation is provided with the following information, prior to the receipt of the waste:


(a)
the nature of the process producing the waste;


(b)
the composition of the waste;


(c)
the handling requirements of the waste;


(d)
the hazard classification associated with the waste; and


(e)
the waste code of the waste.

2.3.3
The operator shall ensure that where waste produced by the activities is sent to a landfill site, it meets the waste acceptance criteria for that landfill.

3
Emissions and monitoring
3.1
Emissions to water, air or land

3.1.1
There shall be no point source emissions to water, air or land except from the sources and emission points listed in schedule 3 table S3.1.

3.1.2
The limits given in schedule 3 shall not be exceeded.

3.2 Emissions of substances not controlled by emission limits
3.2.1 Emissions of substances not controlled by emission limits (excluding odour) shall not cause pollution. The operator shall not be taken to have breached this condition if appropriate measures, including, but not limited to, those specified in any approved emissions management plan, have been taken to prevent or where that is not practicable, to minimise, those emissions.

3.2.2
The operator shall:

(a)
if notified by the Environment Agency that the activities are giving rise to pollution, submit to the Environment Agency for approval within the period specified, an emissions management plan;

(b)
implement the approved emissions management plan, from the date of approval, unless otherwise agreed in writing by the Environment Agency.

3.2.3
All liquids in containers, whose emission to water or land could cause pollution, shall be provided with secondary containment, unless the operator has used other appropriate measures to prevent or where that is not practicable, to minimise, leakage and spillage from the primary container.

3.3
Odour

3.3.1
Emissions from the activities shall be free from odour at levels likely to cause pollution outside the site, as perceived by an authorised officer of the Environment Agency, unless the operator has used appropriate measures, including, but not limited to, those specified in any approved odour management plan, to prevent or where that is not practicable to minimise the odour. 
3.3.2
The operator shall:

(a)
if notified by the Environment Agency that the activities are giving rise to pollution outside the site due to odour, submit to the Environment Agency for approval within the period specified, an odour management plan;

(b)
implement the approved odour management plan, from the date of approval, unless otherwise agreed in writing by the Environment Agency.
3.4
Noise and vibration
3.4.1
Emissions from the activities shall be free from noise and vibration at levels likely to cause pollution outside the site, as perceived by an authorised officer of the Environment Agency, unless the operator has used appropriate measures, including, but not limited to, those specified in any approved noise and vibration management plan to prevent or where that is not practicable to minimise the noise and vibration.

3.4.2
The operator shall:

(a)
if notified by the Environment Agency that the activities are giving rise to pollution outside the site due to noise and vibration, submit to the Environment Agency for approval within the period specified, a noise and vibration management plan;

(b)
implement the approved noise and vibration management plan, from the date of approval, unless otherwise agreed in writing by the Environment Agency.
3.5
Monitoring 

3.5.1
The operator shall, unless otherwise agreed in writing by the Environment Agency, undertake the monitoring specified in the following tables in schedule 3 to this permit:

(a) point source emissions specified in table S3.1; and


(b)
process monitoring specified in table S3.2.


3.5.2
The operator shall maintain records of all monitoring required by this permit including records of the taking and analysis of samples, instrument measurements (periodic and continual), calibrations, examinations, tests and surveys and any assessment or evaluation made on the basis of such data.
 3.5.3
Monitoring equipment, techniques, personnel and organisations employed for the emissions monitoring programme and the environmental or other monitoring specified in condition 3.3.1 shall have either MCERTS certification or MCERTS accreditation (as appropriate), where available, unless otherwise agreed in writing by the Environment Agency.

4
Information

4.1
Records
4.1.1 All records required to be made by this permit shall:

(a) be legible;

(b) be made as soon as reasonably practicable;

(c) if amended, be amended in such a way that the original and any subsequent amendments remain legible, or are capable of retrieval; and
(d) be retained, unless otherwise agreed in writing by the Environment Agency, for at least 6 years from the date when the records were made, or in the case of the following records until permit surrender:

(i) off-site environmental effects; and
(ii) matters which affect the condition of the land and groundwater.

4.1.2
The operator shall keep on site all records, plans and the management system required to be maintained by this permit, unless otherwise agreed in writing by the Environment Agency. 

4.2
Reporting
4.2.1
The operator shall send all reports and notifications required by the permit to the Environment Agency using the contact details supplied in writing by the Environment Agency.
4.2.2
A report or reports on the performance of the activities over the previous year shall be submitted to the Environment Agency by 31 January (or other date agreed in writing by the Environment Agency) each year.  The report(s) shall include as a minimum:

(a)
a review of the results of the monitoring and assessment carried out in accordance with the permit including an interpretive review of that data; 

(b)
the annual production /treatment data set out in schedule 4 table S4.2; and

(c)
the performance parameters set out in schedule 4 table S4.3 using the forms specified in table S4.4 of that schedule.

4.2.3
Within 28 days of the end of the reporting period the operator shall, unless otherwise agreed in writing by the Environment Agency, submit reports of the monitoring and assessment carried out in accordance with the conditions of this permit, as follows:

(a)
in respect of the parameters and emission points specified in schedule 4 table S4.1;

(b)
for the reporting periods specified in schedule 4 table S4.1 and using the forms specified in schedule 4 table S4.4 ; and

(c)
giving the information from such results and assessments as may be required by the forms specified in those tables.

4.2.4
The operator shall, unless notice under this condition has been served within the preceding four years, submit to the Environment Agency, within six months of receipt of a written notice, a report assessing whether there are other appropriate measures that could be taken to prevent, or where that is not practicable, to minimise pollution.

4.3
Notifications
4.3.1
The Environment Agency shall be notified without delay following the detection of:

(a) any malfunction, breakdown or failure of equipment or techniques, accident, or  emission of a substance not controlled by an emission limit which has caused, is causing or may cause significant pollution;

(b) the breach of a limit specified in the permit; or 

(c) any significant adverse environmental effects.  

4.3.2
Any information provided under condition 4.3.1 shall be confirmed by sending the information listed in schedule 5 to this permit within the time period specified in that schedule.
4.3.3
Where the Environment Agency has requested in writing that it shall be notified when the operator is to undertake monitoring and/or spot sampling, the operator shall inform the Environment Agency when the relevant monitoring and/or spot sampling is to take place. The operator shall provide this information to the Environment Agency at least 14 days before the date the monitoring is to be undertaken.

4.3.4
The Environment Agency shall be notified within 14 days of the occurrence of the following matters, except where such disclosure is prohibited by Stock Exchange rules: 

Where the operator is a registered company:

(a) any change in the operator’s trading name, registered name or registered office address; and
(b)
any steps taken with a view to the operator going into administration, entering into a company voluntary arrangement or being wound up.

Where the operator is a corporate body other than a registered company:

(a) any change in the operator’s name or address; and

(b) any steps taken with a view to the dissolution of the operator.

In any other case: 

(a) the death of any of the named operators (where the operator consists of more than one named individual); and

(b) any change in the operator’s name(s) or address(es).

4.3.5
Where the operator proposes to make a change in the nature or functioning, or an extension of the activities, which may have consequences for the environment and the change is not otherwise the subject of an application for approval under the Regulations or this permit:

(a) the Environment Agency shall be notified at least 14 days before making the change; and

(b) the notification shall contain a description of the proposed change in operation.

4.3.6
The Environment Agency shall be given at least 14 days notice before implementation of any part of the site closure plan.

4.4
Interpretation
4.4.1
In this permit the expressions listed in schedule 6 shall have the meaning given in that schedule.
4.4.2
In this permit references to reports and notifications mean written reports and notifications, except where reference is made to notification being made “without delay”, in which case it may be provided by telephone. 

Schedule 1 - Operations 

	Table S1.1 activities
	
	

	Activity listed in Schedule 1 of the EP Regulations 
	Description of specified activity
	Limits of specified activity 

	Section 1.1, Part A(1)(b)(iii) - Burning waste as a fuel in an appliance with a rated thermal input of 3 MW or more but less than 50 MW 


	The combustion of biogas in combined heat and power (CHP) engines and boilers for the production of steam, hot water and electricity.


	From receipt of biogas to export of electricity. 

The CHP engines shall consist of no more than two spark ignition engines with a maximum aggregate flow rate of  9,216 Nm3/hr, (7.49 MWth, 3.12 MWe).

The boilers shall use biogas for supplementary firing and shall consist of no more than two boilers with a natural gas rated aggregate thermal capacity of 7.8 MW.

	Directly Associated Activity

	Operation of a biogas flare
	The flaring of biogas
	From the receipt of the biogas to the release of combustion products from the flare stack 

	Storage and handling of wastes, including waste oils
	Waste storage
	From the generation of the waste through to its removal from the Installation.
Only empty storage containers shall be stored in the open skips described in Section 2.5, Table 6 of the Supporting Information submitted as part of the application.

	Biogas storage
	Storage of biogas arising from the Advanced Digestion process at Afan WwTW 
	Storage of biogas prior to combustion in the CHP engines, supplementary firing in the boilers or flaring. 

	Surface water drainage
	Surface water drainage
	Discharge of site surface water to Afan WwTW

	Water treatment and conditioning
	Boiler water treatment and conditioning
	From receipt of raw materials to discharge of effluent to Afan WwTW


	Table S1.2 Operating techniques

	Description
	Parts
	Date Received

	Application
	Section 5 of the Part B Application Form
	20/10/09, (duly made 27/11/09)


Schedule 2 - Waste types, raw materials and fuels

	Table S2.1 Raw materials and fuels
	

	Raw materials and fuel description 
	Specification

	-
	-


Schedule 3 – Emissions and monitoring

	 Table S3.1  Point source emissions to air – emission limits and monitoring requirements

	Emission point ref. & location (as identified onsite plan at Schedule 7)
	Source
	Parameter  
	Limit (mg/Nm3)1 


	Reference 

period
	Monitoring frequency 
	Monitoring standard or method 

	A1- CHP unit 1
A2- CHP unit 2

	Exhaust of spark ignition engines via individual, 24m  unimpeded vertical stacks
	Nitrogen Oxides (NOx expressed as NO2)
	500
	Hourly Mean
	Annually.

The first annual monitoring to be undertaken as part of the engine commissioning
	In accordance with Agency guidance note 

M2 “Monitoring of stack emissions to air”.


	
	
	Carbon Monoxide 
	1,400
	
	
	

	
	
	Sulphur dioxide 
	339
	
	
	

	A3 - Boiler unit 1

A4 - Boiler unit 2 
	Combustion products from boilers emitted via individual, 24m  unimpeded vertical stacks
	Nitrogen Oxides (NOx expressed as NO2)
	170
	Hourly Mean
	Annually 2
	

	
	
	Carbon Monoxide 
	75
	
	
	

	
	
	Sulphur dioxide 
	160
	
	
	

	A5 - biogas flare with a combustion temperature of  at least 1,000 oC and a residence time of at least 0.3 seconds 
	Combustion products from biogas flare via a 7.5m unimpeded vertical stack


	Nitrogen Oxides (NOx expressed as NO2)
	150
	Hourly Mean
	Annually 3
	

	
	
	Carbon Monoxide 
	50
	
	
	

	
	
	Sulphur dioxide 
	339
	
	
	

	
	
	Operational temperature
	>1000oC
	Instantaneous reading
	Annually 3
	


1 These limits do not apply during start up and shut down.
2 Annual monitoring of the boilers is only required if notified by the Agency, (based on a percentage usage of supplementary firing on biogas). 
3 Annual monitoring is only required when flare operates in excess of 10% of the time, taken on an annual assessment period.
	Table S3.2  Process  monitoring requirements

	Emission point reference or source or description of point of measurement
	Parameter
	Monitoring frequency 
	Monitoring standard or method 
	Other specifications 



	Biogas feed to combustion plant 


	Hydrogen sulphide
	Continuous
	-
	Monitoring location to be agreed in writing with the Environment Agency


Schedule 4 - Reporting

Parameters, for which reports shall be made, in accordance with conditions of this permit, are listed below. 

.
	Table S4.1 Reporting of monitoring data

	Parameter
	Emission or monitoring point/reference
	Reporting period
	Period begins

	Oxides of nitrogen

Parameters as required by condition 3.5.1
	A1, A2, A3*, A4*, A5*
	Annual 
	26/05/10

	Carbon Monoxide 

Parameters as required by condition 3.5.1
	A1, A2, A3*, A4*, A5*
	Annual
	26/05/10

	Sulphur dioxide

Parameters as required by condition 3.5.1
	A1, A2, A3*, A4*, A5*
	Annual 
	26/05/10

	Total VOCs
Parameters as required by condition 3.5.1
	A1, A2, A3*, A4*, A5*
	Annual 
	26/05/10

	Non-methane VOCs
Parameters as required by condition 3.5.1
	A1, A2, A3*, A4*, A5*
	Annual 
	26/05/10

	Hydrogen sulphide concentrations in biogas feed above 1,000 ppmv
	Monitoring point as agreed under table S3.2 above
	Every 3 months
	26/05/10


*as required
	Table S4.2: Annual production/treatment
	

	Parameter 
	Units 

	Electrical energy generated 
	MWhe

	Thermal energy generated 
	MWhth


	Table S4.3 Performance parameters

	Parameter
	Frequency of assessment
	Units

	Total biogas input into the CHP engines 
	Annually
	MWh (gross calorific value)

	Total biogas input into the boilers
	Annually
	MWh (gross calorific value)

	Engine and boiler efficiency 
	Annually
	%

	Hours of operation for CHP engines
	Annually
	hours

	Operational hours of the flare
	Annually
	hours

	Operational hours of boilers supplementary fired on biogas
	Annually
	hours and %

of total operational hours

	Abnormal operation of pressure release valves to be reported to the Environment Agency
	Continuous
	-

	Water usage
	Annually
	m3


	Table S4.4 Reporting forms

	Media/

parameter
	Reporting format
	Date of form

	Emissions to air
	Form Air 1 or other reporting format to be agreed in writing with the Environment Agency
	26/05/10

	Water usage
	Form Water usage 1 or other reporting format to be agreed in writing with the Environment Agency
	26/05/10

	Energy generation
	Form Energy 1 or other reporting format to be agreed in writing with the Environment Agency
	26/05/10

	Biogas input, operational hours and efficiency of various combustion plant. Abnormal operation of PRVs, 
	Form Performance 1 or other reporting format to be agreed in writing with the Environment Agency
	26/05/10


Schedule 5 - Notification 

These pages outline the information that the operator must provide. 

Units of measurement used in information supplied under Part A and B requirements shall be appropriate to the circumstances of the emission. Where appropriate, a comparison should be made of actual emissions and authorised emission limits.

If any information is considered commercially confidential, it should be separated from non-confidential information, supplied on a separate sheet and accompanied by an application for commercial confidentiality under the provisions of the EP Regulations.

Part A 
	Permit Number
	

	Name of operator
	

	Location of Facility
	

	Time and date of the detection 
	


	(a) Notification requirements for any malfunction, breakdown or failure of equipment or techniques, accident, or emission of a substance not controlled by an emission limit which has caused, is causing or may cause significant pollution

	To be notified within 24 hours of detection

	Date and time of the event
	

	Reference or description of the location of the event 
	

	Description of where any release into the environment took place
	

	Substances(s) potentially released
	

	Best estimate of the quantity or rate of  release of substances
	

	Measures taken, or intended to be taken, to stop any emission
	

	Description of the failure or accident.
	


	(b) Notification requirements for the breach of a limit

	To be notified within 24 hours of detection unless otherwise specified below

	Emission point reference/ source
	

	Parameter(s)
	

	Limit
	

	Measured value and uncertainty
	

	Date and time of monitoring
	

	Measures taken, or intended to be taken, to stop the emission
	


	Time periods for notification following detection of a breach of a limit

	Parameter
	Notification period

	
	

	
	

	
	


	(c) Notification requirements for the detection of any significant adverse environmental effect

	To be notified within 24 hours of detection

	Description of where the effect on the environment was detected
	

	Substances(s) detected
	

	Concentrations of substances detected
	

	Date of monitoring/sampling
	


Part B - to be submitted as soon as practicable
	Any more accurate information on the matters for notification under Part A.
	

	Measures taken, or intended to be taken, to prevent a recurrence of the incident
	

	Measures taken, or intended to be taken, to rectify, limit or prevent any pollution of the environment which has been or may be caused by the emission
	

	The dates of any unauthorised emissions from the facility in the preceding 24 months.
	


	Name*
	

	Post
	

	Signature
	

	Date
	


* authorised to sign on behalf of Dŵr Cymru Cyfyngedig 

Schedule 6 - Interpretation 

 “accident” means an accident that may result in pollution.

“annually” means once every year.
“application” means the application for this permit, together with any additional information supplied by the operator as part of the application and any response to a notice served under Schedule 5 to the EP Regulations.

“authorised officer” means any person authorised by the Environment Agency under section 108(1) of The Environment Act 1995 to exercise, in accordance with the terms of any such authorisation, any power specified in section 108(4) of that Act.

 “EP Regulations” means The Environmental Permitting (England and Wales) Regulations SI 2010 No.675 and words and expressions used in this permit which are also used in the Regulations have the same meanings as in those Regulations.

“emissions of substances not controlled by emission limits” means emissions of substances to air, water or land from the activities, either from the emission points specified in schedule 3 or from other localised or diffuse sources, which are not controlled by an emission or background concentration limit..
“groundwater” means all water, which is below the surface of the ground in the saturation zone and in direct contact with the ground or subsoil.

“MCERTS” means the Environment Agency’s Monitoring Certification Scheme.

“quarter” means a calendar year quarter commencing on 1 January, 1 April, 1 July or 1 October.

“year” means calendar year ending 31 December.
Where a minimum limit is set for any emission parameter, for example pH, reference to exceeding the limit shall mean that the parameter shall not be less than that limit.

Unless otherwise stated, any references in this permit to concentrations of substances in emissions into air means:

(a) in relation to emissions from combustion processes, the concentration in dry air at a temperature of 273K, at a pressure of 101.3 kPa and with an oxygen content of 3% dry for liquid and gaseous fuels, 6% dry for solid fuels; and/or

(b) in relation to emissions from non-combustion sources, the concentration at a temperature of 273K and at a pressure of 101.3 kPa, with no correction for water vapour content

Schedule 7 - Site plan

[image: image3.jpg]


Location plan

. 

Reproduced from the Ordnance Survey map with the permission of the Controller of Her Majesty’s Stationery Office (Crown Copyright 2000. Unauthorised reproduction infringes Crown Copyright and may lead to prosecution or civil proceedings.

Site layout plan
[image: image1.jpg]



Reproduced from the Ordnance Survey map with the permission of the Controller of Her Majesty’s Stationery Office (Crown Copyright 2000. Unauthorised reproduction infringes Crown Copyright and may lead to prosecution or civil proceedings.

END OF PERMIT

PAGE  
	Permit Number   EPR/ZP3032KQ
	  Page 9
-  -
- 9 -
- 9 -9 
	Date of issue: 26/05/10



