SOUTH WALES WOOD RECYCLING LTD
FIRE RISK ASSESSMENT

March 2016
CONTENTS

Introduction – Fire Risk Assessment 

Section 








   

1 Premises Particulars

2 General Statement of Policy

3


Management Systems
4


General Description of Premises

5 Fire Safety Systems within the premises 




6 Plan Drawing




       

7


Fire Hazards

8  


People at Risk

9 Means of Escape (Horizontal Evacuation)

10


Means of Escape (Vertical Evacuation)

11 Fire Safety Signs and Notices

12 Fire Warning System

13 Emergency lighting

14 Fire Fighting Equipment
15 Maintenance

16 Method of calling the Fire Service

17 Emergency Action Plan

18 Training

19 Record of Fire Safety Deficiencies

20 Significant Findings

21 Additional Hazards

	FIRE RISK ASSESSMENT

	1
	PREMISES PARTICULARS

	Premises Name: South Wales Wood Recycling Ltd
Address: Locks Yard, Heol Llan, Coity, Bridgend, CF35 6BU
Tel no: 01656 865303
	Use of Premises

OFFICES & SEPARATE WORKSHOPS AND PROCESSING BUILDING


	
	Owner/Employer/Person in control of the workplace: George Harvey


	Date of Risk

Assessment March 2016

	Date of

Review MARCH 2017 (unless changes to building/activities etc.)


	Name & relevant details of the person who carried out the Fire Risk Assessment

P. REES – CMIOSH, RSP

G Harvey – IOSH, COTC, WAMITAB  LEVEL 4



	2
	GENERAL STATEMENT OF POLICY

	Statement:
REFER TO COMPANY H&S POLICY STATEMENT
Signed:



Print Name:



Date:




	3
	MANAGEMENT SYSTEMS

	Commentary:

Planning:

An audit was performed in conjunction with this document and appropriate checklists as indicated within the Fire RA file. Site plans were produced to determine the location of hazards, access points and fire control points.
Organisation:

The Company is structured as that indicated within the PAS 402 Management System manual with an organogram depicting the set up and areas of responsibility.

Health & safety information is communicated via toolbox talks, notice boards, contact and periodic training arrangements.

Employees are made aware of fire arrangements by the fire action notices displayed within the buildings and contributing to periodic fire drills. It is also contained within their Safe Systems of Work booklets.
Control:

The H&S manual and displayed documents/notices identify the responsibilities of those within the buildings.

This includes: management, fire marshal, first aiders and other nominated persons.

Monitoring:

An external audit of the facilities will be performed on at least an annual basis by the H&S advisor/consultant and a report submitted to management. Any corrective/preventive actions will be adequately documented and closed out.
Other site monitoring includes a weekly review/record of fire precautions arrangements normally performed by the MD and/or a nominated person e.g. fire marshal.

Information is exchanged informally as it occurs and formally at the preset training days/management meetings.

Review:

All procedures are regularly reviewed via informal and/or formal arrangements and the appropriate actions taken to remediate/rectify.



	4
	GENERAL DESCRIPTION OF PREMISES

	Description:

Building 1 - the main internal processing shed consists of a large single building with ACM to the roof and sides. The floor is concrete and the building houses unprocessed clean wood waste material and processed wood chip material. Stockpiles are rotated regularly and product stored for no longer than 48 hours.
Building 2 – consists of a Workshops that are used for vehicle and plant maintenance. They also have ACM sheeting on sides and roof. The contain hazardous chemicals commonly found in workshops. Diesel is also stored in a lean to one of the workshops and accessed via a side door. The main workshop area also contain an air receiver and compressor with a pressurized line running around the inside of the building. A mess room is also contained within this building.
Building 3 – consist of the main site offices.  
Both the processing building and the workshops are 15 years old and constructed of steel framework with ACM / concrete sheeting to the roof and sides. The Office building is steel construction and clad in a brick exterior. It is also approximately 15 years old.
Open Yard area – this area is used for the majority of the receipt, processing and stockpiling of recycled waste wood material.


	Occupancy

Times the Premises are in use:
8am
to 6pm
The Total Number of persons Employed

within the premises at any one time:  26
The Total Number of persons who may

resort to the premises at any one time:

26
	Size

Building footprint 50m x 25m
(Metres x Metres):

Number of floors:

Main office building – two floors
Separate workshop and processing building – first floor only

Number of Stairs:
Office building – one

Workshop – one


	5
	FIRE SAFETY SYSTEMS WITHIN THE PREMISES

	Fire Warning System:  (i.e. automatic fire detection, break-glass system to BS 5839, other)
A number of smoke and/or fire detection detectors are installed as per the enclosed plans.

A number of break-glass systems are installed as per the enclosed plans.

The fire alarm control panel is located within the main conference room area and as the site plan.



	Emergency Lighting:  (i.e. maintained/non-maintained, 1hr/3hr duration to BS 5266)
Emergency lighting is installed and is subject to regular inspection and records retained.  

	Other:  (i.e. Sprinkler system to LPC rules BS 5306)
A number of fire extinguishers are located at recommended locations as installed/maintained by a competent supplier and as per the site plans.

Fire sounders are installed as per the site plans to alert employees of the need for emergency action and evacuation.  




	6
	PLAN DRAWING

	PLEASE REFER TO ATTACHED PLANS FOR BUILDING LAYOUT



	7
	IDENTIFY FIRE HAZARDS

	Sources of Ignition:

Plant and Machinery – daily maintenance and servicing

Stockpiles – regular rotation and movement

Waste material – permit control and inspections

Electrical installation, fixed and portable equipment – these are periodically PAT tested.
Gas boiler – maintained/inspected

Cooking equipment – microwaves, toaster – PAT tested
Lighting units – segregated storage
Arson – intruder alarm in use and CCTV footage


	Sources of Fuel:

Flammable liquids stored/used within the laboratory – COSHH assessment and limited storage outside of steel approved storage cabinet – less than 50 litres stored within the workplace e.g. Acetone, Propanol.
Waste materials are stored in line with permit conditions and removed regularly.
Normal office consumables and stored within the main office and/or dedicated storage areas.


	Work Processes:

The business processes up to 8000 tonnes of waste wood per month. This includes civic amenity wood, construction and demolition wood as well as broken pallets and cases. Over 200 skips around South Wales & England and walking floor trailers collect all types of waste wood from factories, various construction and demolition firms and civic amenity sites. All timber is shredded and screened giving many different products for supplying chipboard factories, carbon neutral power stations and for animal bedding.

We are committed to continually improving our environmental, health & safety and quality aspects of our operation by operating to the clauses laid out in PAS 402:2013.



	Work Processes:

Normal office activities. 
1. Stockpiling of the product shall be largely in accordance with current guidelines.
2. Stockpile height will vary but should not exceed 5m high. Due to site restrictions the width of stockpiles are unlikely to exceed 20m and are normally no more than 10m.
3. Stockpiles will be at least 6m from any building

4. Stockpiles will not be stacked within 6m of combustible materials or ignition points. Where product is to be stored close to surface water drains, action must be taken to avoid entry into the drains/watercourse.

5. Work will be arranged in such a way as to not have any vehicle congestion at the stockpiling area.
6. Pedestrians will be restricted from the working area.
7. Spillage of product must be cleaned up immediately and disposed of. Machine buckets should not be overfilled, minimizing any possibility of material spillage.
8. Vehicles / machinery should not be allowed to park in the vicinity of the stockpiles and will in any event be kept at least 6m away from stockpiles when parked. Any vehicle oil / diesel leaks must be reported immediately and not allowed to work the product.
9. If required, product should be monitored on a regular basis for temperature. This would normally occur if any material remains on site for longer than 3 months without moving. Where temperature exceeds 65 degrees Celsius, the material must be rotated and allowed to cool. Further regular turning of the product shall be carried out to aid cooling. All monitoring, inspections and action taken shall be recorded.
10. All personnel involved in the handling of the product shall undergo appropriate training and instruction relative to their roles and receive regular tool box talks, especially where there is a change of personnel, procedures or equipment.
11. In addition to the mandatory site PPE, goggles and masks shall be provided for use in dusty / windy conditions.
12. All personnel should be reminded of the site rules on smoking and hygiene.
13. All hotwork to be carried out on site shall be under permit to work conditions

Addition measures / detail:

Fire Prevention Guidance from Guidance Note issued by Natural Resources Wales in March 2016
Product Control

· Wherever possible, material will be processed the same day that it comes into site. If it is not able to be processed the same day, it will be processed the following day and then stockpiled.

· Any metals that may create the possibility of heating in damp conditions will be controlled by the removal during processing prior to delivery.

Storage Methods

· Stockpile heights will vary but should not exceed 5m and any stack will be kept at least 6m away from any structure or flammable material store. Due to site restrictions the width of stockpiles are unlikely to exceed 20m and are normally no more than 10m.
· The maximum tonnage storage capacity is 2,500tns for the site at any one time. This is normally held in a number of stockpiles around the site and made up of processed and unprocessed material.

· The largest stockpile of material will be the material to go to the board mills / export operations. This can be up to 1500tns at any one time. Although contrary to the guidance, the throughput of this material is generally very quick and it is highly unlikely that any material remains on site for longer than 3 months.

· There also exists the plant and machinery capability to address an issue rapidly should the need arise. Due to the width and height restriction, separating the material would be extremely quick. As such, the risk of fire in a stack this size is minimal and the response time extremely quick.
· The stockpiles will be regularly moved either for stock rotation or loaded into lorries for delivery to other sites and customers. No material will remain on site without being rotated or loaded for transport for longer than 3 months. 
· Access to all areas of the site will be maintained at all times.
Preventative Action

· The stacks will be routinely monitored by staff and any ‘unusual behavior’ reported and acted upon. The site will also be routinely inspected.

· The site is also monitored on a 24 hour 7 day a week basis and operatives are available on call as and when the need should arise. This is undertaken on a rota basis to ensure cover is always maintained and response times are within 15 minutes from contact.
· Staff and contractors on site will follow safe working practices when undertaking hot working

· Visitors will follow the correct safety and fire prevention procedures

· The area is strictly non smoking with appropriate signage erected.

· Access to the site is controlled to reduce the chance of arson by a site security office upon entrance to the port and also site security fencing surrounding the perimeter of the site.

· All plant and machinery is regularly maintained and never parked in the vicinity of the stockpiles. Plant and machinery is only ever operated by suitably trained operatives.

· All plant and machinery is fitted with fire extinguishers and dust filters

· An emergency quarantine area is available at the entrance of the site and is available at all times.

Fire Prevention / Response Plan

· The site will observe health and safety procedures and comply with fire regulations. Staff will be suitably trained.

· Advice will be sought from local Fire & Rescue Service on the appropriate provision of fire extinguishing devices

· Heavy plant and machinery is available and will be used as necessary.

· Fire hydrants have been identified and are 100m from the site entrance and will remain accessible at all times. The site has a dedicated fire engine with a water supply and 1800ltr capacity. Two 20,000 litre underground tanks are also available
· All drainage lines on site are sealed so in the event of an incident minimal the potential for firewater runoff pollution is minimal. All water would be recirculated for dust suppression and fire control. Failing that it would be tinkered off site.



	8
	IDENTIFY PEOPLE AT RISK

	Identify and specify the likely location of people at significant risk in case of fire, indicating why they are at risk, and what control’s are or need to be in place:

Employees:
Access/egress to and from the building is controlled via site personnel and visitor book. Doors are locked and only employees have keys. 
The Company is not aware of any disabilities etc which could cause issues under emergency situations.

Within the separate office building the employees have fire escapes at both ends of the building. The ground floor has an exit through the main door and fire exist through bottom offices.
An employee register is to be maintained and held in the reception area to be collected and cross checked versus knowledge of those on site. 

Visitors etc:

Access is controlled via visitor book and site instruction govern the activities allowed on site. All visitors are supervised and accompanied when required.

Contractors:
Contractors made aware of emergency arrangements and an assessment made upon the work to be performed. 
Limited lone working is performed however there is a lone working system and RA for such.



	9
	MEANS OF ESCAPE – HORIZONTAL EVACUATION

	Commentary:

· Fire hazards are controlled by employees and site management via cursory inspections
· Emergency and fire arrangements are performed at least monthly and recorded as per the documented system included within this plan.

· Induction records are used for all employees particularly for new and temporary site users. 
· During fire drills the time for escape has been noted and no problems having been indicated with travel distance being short.

· The storage of combustible materials and the use of closed doors for rooms off the escape routes should not inhibit safe evacuation in an emergency.

· Emergency escape routes and doorways are well signed, even with emergency lighting, with adequate width for the number of employees present.

· The separate first floor building has two exits
· Corridors etc are adequately constructed as to allow safe exiting.

· The main entrance door is manually operated and access/egress allowed in the event of an emergency situation.

· Housekeeping is part of the regular site monitoring/checking arrangements and immediate action taken as required – personnel are to be continually briefed on storage and access needs.

· Stockpiles are kept clear of access routes and away from buildings.

· Workshops have access and egress from both ends of the buildings as well as the side.



	10
	MEANS OF ESCAPE – VERTICAL EVACUATION

	Commentary:

· Within the main office building the stairwell is not inhibited in the event of evacuation and is protected by fire detectors.
· The exit is immediately located at the foot of the stairwell allowing immediate and unobstructed egress, except for a fire door. This is not expected to be a problem due to the number of people affected. It is understood that the doors are of fire resisting construction and is indicated within the building plans accompanying this document.




	11
	FIRE SAFETY SIGNS & NOTICES

	Commentary:
The existing emergency exit and illuminated signage is adequate.

Nevertheless it has been acknowledged that further signage is required:

· Small signs for flammable chemicals

· Fire exit signs in the workshop area

· Fire-exit keep clear signs for the fire exit to the workshop building
The emergency plan is to be updated in conjunction with this RA.



	12
	FIRE WARNING SYSTEM

	Commentary:

There is an adequate warning system designed to the BS to include detectors, sounders and break glass units. It is acknowledge that these need updating but this does not present a significant risk in view of the number of employees working in the office building and the location of the existing alarms.
The position/location of these can be observed upon the site plans included in this document and whereupon periodic checking is performed and recorded.


	13
	EMERGENCY LIGHTING SYSTEM

	Commentary:

Emergency/escape lighting units are installed in line with the BS and building control which are periodically checked/recorded for operation and use. These units have battery back-up which is also checked for correct operation and length of use. 


	14
	FIRE FIGHTING EQUIPMENT

	Commentary:

The existing firefighting equipment has been approved by a competent installation company and is subject to annual checks and upgrades as appropriate.

They are strategically positioned and the condition, pressure indicators etc subject to periodic inspection under the routine checking system and recorded. 

These are only to be used by competent persons and/or in the event of an emergency to allow escape without putting other lives at risk. 
It has been acknowledged that there are no fire blankets within the kitchen areas and are to be obtained and installed ASAP.
A fire engine is on site and has a high pressure hose system capable of holding 1800 liters of water.

A sprinkler system is also used on site for dust suppression and can be used for fire suppression. They are linked to two 20,000 liter tanks located at the rear of the yard. These can be seen on the site plans.




Recommended maintenance schedule

	Equipment
	Period
	Action

	
	
	

	Fire detection and fire warning systems including self-contained smoke alarms and manually operated devices.


	Weekly
	Check all systems for state of repair and operation. Repair or replace defective units Test operation of systems, self contained alarms and manually operated devices.

	
	
	

	
	Annually
	Full check and test of system by

Competent service engineer. Clean self-contained smoke alarms and change batteries.

	
	
	

	
	
	

	Emergency lighting equipment

including self-contained units

and torches.


	Weekly


	Operate torches and replace

batteries as required. Repair or

replace any defective unit.

	
	
	

	
	Monthly


	Check all systems, units and

torches for state of repair and

apparent working order.

	
	
	

	
	Annually
	Full check and test of systems

and units by competent service

engineer. Replace batteries in torches.

	
	
	

	
	
	

	Fire-fighting equipment including

hose reels.
	Weekly


	Check all extinguishers including

hose reels for correct installation

and apparent working order.

	
	
	

	
	Annually


	Full check and test by competent

service engineer.


	15
	MANAGEMENT - MAINTENACE

	Is there a maintenance programme for the fire safety provisions in the premises 
Yes / No

Commentary: A fire log book type recording system is in use and is included within this plan.


	Are regular checks of fire resisting doors, walls & partitions carried out 
Yes / No

Commentary:



	Are regular checks of escape routes & exit doors carried out
Yes / No

Commentary: As per fire log record and per competent engineers


	Are regular checks of fire safety signs carried out
Yes / No
Commentary: As per fire log record and per competent engineers


	Is there a maintenance regime for the fire warning system
Yes / No
Commentary: As per fire log record and per competent engineers


	Is there a maintenance regime for the emergency lighting system
Yes / No
Commentary: As per fire log record and per competent engineers


	Is there maintenance of the fire fighting equipment (By competent persons?)
Yes / No
Commentary: As per fire log record and per competent engineers


	Are records kept & their location identified
Yes / No
Commentary: As per fire log record and per competent engineers



	16
	METHOD FOR CALLING THE FIRE SERVICE

	Specify:
This is indicated upon the displayed Fire Action Notices and within the EAP.
In general an outside line has to be obtained via a ‘9’ prior to the ‘999’ call. Calls can also be made from site mobile phones.


	17
	EMERGENCY ACTION PLAN (EAP)

	Commentary:

This is a separate document appended to this fire RA.


	18
	TRAINING

	Commentary:

· The existing EAP is displayed upon the notice board but is to be updated as indicated.
· The induction form has also been updated to reflect additional fire precautions and awareness to include contractors who must inform site management of any activities employed which could compromise the fire precautions and RA e.g. power use, flammable materials, means of escape etc. 

· Fire training is also received via the evacuation and fire drills performed at least on an annual basis.

· Fire marshals are to be re-established/expanded upon with nominated persons being given that task and awareness/training given to follow this plan and the EAP



	19
	FIRE SAFETY DEFICIENCIES TO BE RECTIFIED

	Deficiency/Rectification


	Priority


	Date to be

Rectified


	Date

Rectified



	Update of floor plans to indicate fire precaution installation.
Update fire log/record form for scheduling inspection

Update of induction form to expand upon fire precautions e.g. assembly point

Preparation of updated Emergency Action Plan (EAP)
To erect a sign to indicate assembly point
To identify the fire hydrant for firefighting purposes
To compile register of hazardous chemicals
To source/erect addition ‘fire exit’ signs at means of escape routes and exits

To source/erect ‘fire door-keep clear’ signs on doors exiting the means of escape –workshop
To relocate Asbestos containing waste due to poor access to flammable store and risk of exposure.
To establish an employee register to use as a record/checklist in an emergency situation

To obtain/erect fire blankets within kitchen areas

To nominate a fire marshal to coordinate fire precautions/activities

To source fire engine as a fire suppressant mechanism

RCD installation check


	ASAP
ASAP
ASAP
ASAP
ASAP

ASAP
ASAP
ASAP
ASAP
ASAP
ASAP
ASAP
ASAP
ASAP
ASAP

	1/15
1/15
1/15
1/15
1/15
1/15
1/15
1/15
1/15
1/15
1/15
1/15
1/15
1/15
1/15


	Done – Nov 14
Done – Nov 14
Done – Nov 14
Done – Nov 14



	20
	SIGNIFICANT FINDINGS

	Significant Finding


	Control Measure/Action



	Scheduling of test/inspection of fire precautions
Additional site signage to increase awareness such as for means of escape

No record of RCD installation test/check
Free standing electrical heater in DD office

Ensure doors leading to means of escape routes are closed and no items blocking corridors etc.
Warning signage in reception area incorrectly located
*Insert additional pages as required


	Nominate fire marshal and update fire log/record form
Obtain/erect signage
Arrange RCD installation check/test
Remove to safer location and label area to remove risk of items being stored/placed to close
Improve housekeeping arrangements, educate employees of need to keep clear and report issues.
Move signs to more accessible location



	21
	ADDITIONAL HAZARDS

	Specify:

· Storage of Asbestos wastes
· Waste processing near fire escapes

· Fuels storage

· Gases storage

· Flammables storage



