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Part A 
	Permit Number
	PP3139GB

	Name of Operator
	Enovert North Limited

	Location of Installation
	Bangor Road, Johnstown, Wrexham, LL14 6ET

	Time and date of the detection
	When data entered onto database

	b) Notification requirements for breach of a limit

	To be notified within 24 hours of detection unless otherwise specified

	Emission point reference/source
	Leachate Head
Limit: >2m 
	Sample Point
	Date
	Leachate Head (m)

	HF MP1b
	09/02/2022
	 (Transducer faulty)

	HAF LMP2AR
	23/02/2022
	Hung up at 24.6m

	HAF LC3
	09/02/2022
	1.89 (Transducer)

	HAF LMP4b
	23/02/2022
	17.56

	HAF LC4
	23/02/2022
	13.79 (Transducer level 7.44)




	Parameter(s)
	

	Limit
	

	Measured value and uncertainty
	

	Date and time of monitoring
	

	Measures taken, or intended to be taken, to stop the emission
	The leachate remains contained and no emission from the site is occurring.



Part B
	Any more accurate information on the matters for notification under Part A.
	In February 2074 m3 of leachate was tankered off site for treatment. 
The levels in LMP2AR are considered to be perched. The pump is now fitted in LMP2AR and the dip meter got hung up this week at 24.60m (dry). The pump and transducer are down to a depth of 40m (base 47.4m), the liquid has been pumped down and the transducer is showing the level at 1.5-2.5m above the base of the pump. We will keep the pump at this level for a few weeks, we will then start to lower it in 1m increments. This is to avoid damaging the pump with too much sediment. The level above base is now 9-10m.
The manual dip at LC4 is showing a decrease of 2.53m since January. However on the day it was dipped the transducer was reading 6m below the dipped level.
As stated in the previous S5’s the manual dips in LMP4a and LMP4b are thought to be due to perched levels, however unfortunately we are unable to obtain a manual dip for LMP4a this month and LMP4b is showing an increase of 1.41m. 
New transducers have now been installed in MP4a and MP4b, this will allow us to get readings from the wells when access for manual dipping is unsafe. The transducer readings today are MP4a = 11.44m and MP4b = 11.32m.  We can now record some continuous representative readings from these two chambers.
Work is still ongoing to resolve the reliability issues with the air pump in LMP4b.
Transducer readings have been provided for Cells 1 and 3, where access is unsafe for the monitoring technician. In February a new access ramp has been excavated down to LC3 to provide safe access.

	Measures taken, or intended to be taken, to prevent a recurrence of the incident
	As above.

	Measures taken, or intended to be taken, to rectify, limit or prevent any pollution of the environment or harm which has been or may be caused by the emission
	 
Not applicable as no pollution has been caused because no emission is believed to be occurring.


	The dates of any unauthorised emissions from the installation in the preceding 24 months.
	Please see previous notifications.

	Name*
	Elizabeth Forrest

	Post
	Environmental Data Analyst

	Date
	11.03.2022


* authorised to sign on behalf of Enovert North Ltd



