## Current asset evaluation
Zone 4 - Digested sludge tanks (GFS)
Description | Digestate is pumped for the digesters to the digested sludge tanks. Sludge enters the tanks from the bottom of the tank and sludge is then returned to the centrifuge feed tank through a centrally locate belmouth at the bottom of the tank.
Number of tanks | 2
Volume of tank | 468m3 (approximately) - total volume for each tank Based on discussions, there is no overflow in place for high levels within the tank.
Material of tank | GFS
Above/below ground? | Above ground covered tanks
Pipe material | Connecting pipework appears to be ductile iron – above and below ground pipes.
Drainage for zone | Road to the east drains via gullies to liquors return tank Grassed area around tank infiltrates into ground
Year of construction | Drawings state 1980, but operations state that it was constructed in 2003
Surrounding area | Surrounding external area is primarily grass - permeable
Is asset fit for purpose? | The tanks were originally designed and constructed to hold digested sludge and has been operating with no notable concerns. Tank has not undergone a change of use
Condition of the tank Any tank failures - cracks, flaking, corrosion, overflows, overfilling? | Tank is in good condition and no issues noted from operations Marks on tank are from bird dropping and plant material om top of tank after cleaning
Condition of pipework Pipe leaks, corrosion? | No visible issues/leaks reported by operational staff
Protection of assets - bollards? | No vehicle impact protection
Control/monitoring/alarming measures in place? | No control measures - tanks are manually filled by operations on a day to day basis. No telemetry or alarms Ultrasonic depth meters are in place
Secondary containment provided? | None
Secondary containment condition? | N/A
14/08/2020
File Ref
Version
B14411-123532-ZZ-XX-AS-ZA-CI1005
P01
Originator
Jacques Calitz
James Croston
Date
Date
30/06/2020
14/08/2020
Checker
Zone 4 (Digested sludge holding tanks)
IED CIRIA 736 Risk Assessment
James Croston
Approver
Date

## Zone 4 volume
Diameter | 12.97
Height | 3.54
Volume | 467.7062
14/08/2020
File Ref
Version
B14411-123532-ZZ-XX-AS-ZA-CI1005
P01
Originator
Jacques Calitz
James Croston
Date
Date
30/06/2020
14/08/2020
Checker
Zone 4 (Digested sludge holding tanks)
IED CIRIA 736 Risk Assessment
James Croston
Approver
Date

## Risk assessment
Source
Material | Physical properties | Maximum quantity | units | Storage | Flammability | Corrosive | Ecotoxicity (based on LD and quantity) | Hazard rating
Digested sludge tank 1 | Liquid with sludge <= 4-5% (digestate) | 468m3 (approximately) - total above volume for each tank | m3 | GRP above ground tank | Not flammable | Possibly | Organic heavy - Nitrogen, Phosphorous, Ammonia, BOD, TSS, COD - Environmental hazard (algae blooms and death of organisms) Pathogens - Human hazard (E.coli etc.) | M
Digested sludge tank 2 | Liquid with sludge <= 4-5% (digestate) | 468m3 (approximately) - total above volume for each tank | m3 | GRP above ground tank | Not flammable | Possibly | Organic heavy - Nitrogen, Phosphorous, Ammonia, BOD, TSS, COD - Environmental hazard (algae blooms and death of organisms) Pathogens - Human hazard (E.coli etc.) | M
Rainwater run-off contaminated by inventory | Surface water mixed with sludge/pollutants | Dependent on area of containment | m3 | N/A | Not flammable | No | Lower concentration of sludge contaminants | L
[7 empty] | Overall | M
Pathway and Receptor
Pathway - the route from primary containment to receptor (extent of loss of containment) |  | Time of concentration/ duration of source outside containment |  | Hazard - Transport potential |  |  | Receptor | Hazard - Damage potential
Tanks are surrounded by permeable grass. Based on available ground information, soil is permeable (infiltration rate of 4 x 10-5m/s) Permeable sub-soils/strata will thus act as a pathway |  | Direct contamination but over an extended period of time |  | M |  |  | Groundwater (underlain by a secondary aquifer) - contaminated through percolation through soil or through fluctuating tidal groundwater level Over a very long period, can contaminate river Dee through groundwater base flow underground | M
If permeable area get saturated (high groundwater) or becomes blocked with sludge, areas will act as impermeable and transport sludge downstream. |  | Direct contamination but over an extended period of time |  | M
Tidally fluctuating groundwater |  | Direct contamination but over an extended period of time |  | M
Existing underground services - ductwork, tunnels etc. (locations not known) |  | Direct contamination but over an extended period of time |  | L
Existing underground sludge pipework |  | Direct contamination but over an extended period of time |  | M
There is impermeable tarmac road surfacing north of the tanks. If inventory is cascaded onto road (saturated permeable ground), sludge will be transported downstream along the road surface into the road gullies and into the site drainage system (liquor return) |  | Minutes - hours |  | H |  |  | WWTW - liquor return tank pumps liquor back to head of works In the case of a catastrophic failure, volume will cascade to the low point which is the humus tanks.
*Flood water - Site is within flood zone 3 (operational staff did however mention no flooding has been recorded within the site) |  | Minutes - N/A (dependant on flooding extent) |  | L |  |  | River Dee - animals and fish (320m away) | H
|  | Overall |  | M |  |  | Overall | M
*Flooding in flood zone 3 only have a 1 in 100 year probability of happening in a year
Combination of Hazards | MMM
Overall risk rating for zone (Ciria 736) | M
Frequency of loss of containment
Failure mode | Description | Existing consequence and mitigation measure | [6 empty] | Annual probability of loss of containment | Rating
Operational failure - tank (partial) | Overfilling/overflow of tank | Each digester spills 80 - 100m3 of digestate to the digested sludge holding tanks each day. The filling of the zones is controlled manually by operational staff. Zones are filled on a zone by zone basis. Based on the digester feed pumps, the gravity flow rate to the digested sludge holding tanks would be 8-10l/s (4-5l/s per digester feed pump). Operational staff have not reported any cases of overflows and both tanks are covered. Both tanks have high level overflows, but based on discussions with operational staff, the overflows are not in operation and valves are closed. The level within the tanks are monitored by ultrasonic level sensors, but not linked to Scada or alarmed. In the unlikely event if there is an overflow, the volume lost would be minimal (assumed <29m3 based on hourly flow rate to holding tanks). As currently filling is done manually, spills would be limited to a low volume as valves can be shut with relative ease by operational staff filling the tanks. Each tank is filled individually. Total loss of containment is not credible when considering overflowing or foaming of the tank (partial loss of containment would be more likely to occur but is still very unlikely). | [6 empty] | 1 in 100 to 1 in 1 Million | M
Structural failure - tank (catastrophic) | Catastrophic failure due to significant external damage Most likely failure is through the base at the junction between the tank and the concrete base. Potential to lose total volume if above ground connecting pipework fails/break off of tank - has been a failure mode for GFS tanks in the past | Tanks are located above ground. In the case of significant damage above ground, the total volume contained above ground could be lost. It is however very unlikely for the tanks to fail catastrophically structurally as the tanks are fit for purpose. Sludge could be lost if the seal and connection between the tank and slab fails catastrophically. There have been cases in the past where the total above ground volume was lost through the base of the tank when the seal failed. GFS tanks have in the past also had the pipe connections to the tank fail (mixer connection), causing a rupture/hole in the tank, through which the total inventory is lost. The existing high level overflow connecting pipework is located at ground level, the tank could potentially lose its total above ground volume through the hole if the pipework were to break off the tank (very unlikely). There are no credible scenarios that could lead to a catastrophic failure of the digesters (partial loss of containment would be more likely to occur but still very unlikely). | [6 empty] | > 1 in 1 Million | L
Structural failure - tank (partial) | Loss of containment most likely to occur where there are weak points in the tank - Most likely through failures where pipe connects with the structure, bolts/sealant between panels or pitting in the tank. Weak points could be created through either human damage (during maintenance/operation) or environmental (corrosion) | Tanks are located above ground. Any significant loss of containment, would spill above ground. Structural failure of the tank would mainly be through corrosion (bolts, connections between panels). In the case of significant corrosion and leaks forming above ground, the volume contained above ground would seep through the leaks. The tank could potentially lose the above ground volume over a long period of time (very unlikely). Due to operational presence on site, large drops in levels in the tanks and significant leaks above ground would be noticed. Significant corrosion below/above ground would also be easily spotted if tank is inspected. There are no credible scenarios that could lead to a catastrophic failure of the digesters (partial loss of containment would be more likely to occur but still very unlikely). | [6 empty] | 1 in 100 to 1 in 1 Million | M
Structural failure - pipework (catastrophic) | Loss of containment due to failure of above ground connecting pipework | In the extremely unlikely event where the above ground pipework or valves in the chambers fail completely. A significant volume could be lost if the valves are not closed by operational staff or tanks are not drained down to limit loss of containment. As the site is generally manned, valves would be closed and operated by operational staff if the pipes were to fail. In the case where critical pipework fails and valves cannot mitigate the spillage, the tank could lose its full volume. There are no credible scenarios that could lead to a catastrophic failure of the pipework (partial loss of containment would be more likely to occur but still very unlikely). | [6 empty] | > 1 in 1 Million | L
Structural failure - pipework (partial) | Loss of containment most likely to occur where there are weak points in the pipework - Most likely through failures where pipe connects with the structure, bolts/sealant at pipe flanges/valves or along any pipe pitting. Weak point could be created through either human damage (during maintenance/operation), erosion (high velocities and silt content within the pipe) or environmental (corrosion) | Majority of pipework, connections and chambers are located below ground (cast and ductile iron). Some of the connecting pipework is located above ground. If loss of containment occurs underground, sludge will percolate into the soil at a slow rate over a long period. If significant leaks, localised wet areas will be present above ground. If loss of containment occurs above ground through leaks or damage to pipework, due to the permeable grass around tank, sludge will also percolate into the soil at a slow rate over a long period. Due to operational presence on site, significant leaks (above or below) ground would be noticed and loss of containment would be mitigated through operational measures (closing of valves). No significant leaks were mentioned by operational staff. Total loss of containment is therefore not deemed to be a credible scenario. Partial loss of containment is possible but still highly unlikely when considering larger volumes. | [6 empty] | 1 in 100 to 1 in 1 Million | M
Vehicular impact (partial to catastrophic) | Impact from vehicles - damage to pipes or tank causing loss of containment | No known vehicle impacts - but no barrier/protection Vehicles could potentially impact and damage GFS tank which is located above ground. Vehicular impact could cause Significant damage to the tank causing the total volume to be lost. The GFS tanks would not be able to sustain a horizontal impact especially high speed collisions. Vehicles are however unlikely to impact the tanks due to their location. Total loss of containment is therefore not deemed to be a credible scenario. | [6 empty] | 1 in 100 to 1 in 1 Million | M
Vandalism | Vandalism of infrastructure - damage to pipes or tank causing loss of containment | No known vandalism to tanks or pipework - CCTV cameras on site. Thefts in the past based on comments from operators but not damage to any of the assets on site. If vandalism damage were to occur, total loss of containment is unlikely. Partial loss of containment would be more likely to occur if slight damage was done. | [6 empty] | > 1 in 1 Million | L
Flooding | River flooding - Flood zone 3 - - damage to pipes or tank causing loss of containment | No flooding has been reported/recorded by the operators Even if flooding occurred, tanks will not be damaged and full volume of sludge will not be lost. There could be a potential for the flood water to be contaminated. The flood water could enter the below ground chambers around the tanks and potentially get contaminated. | [6 empty] | > 1 in 1 Million | L
*Site is manned. Probability and frequency thus reduced
Frequency of loss of containment (Ciria 736) | M
Overall zone hazard rating
Overall zone hazard rating (Ciria 736) | Moderate
Containment required
Containment required | Class 2
180m
120m
320m
River Dee
Liquor return at head of works
3rd party land
Ditch
200m
Permeable ground
Impermeable ground (tarmac)
Low point
Road gullies
Overland flow paths
Permeable ground (paved)
Failure at tank side - liquor return pipe breaks away from tank - Assumed pipe will completely fail and leave a hole that acts as an orifice
Failure of valve/pipe at digestate inlet manhole upstream of tank - most likely will be a slow rate of loss of containment
Failure of valve/pipe at digestated sludge return manhole downstream of tank - most likely will be a slow rate of loss of containment
14/08/2020
File Ref
Version
B14411-123532-ZZ-XX-AS-ZA-CI1005
P01
Originator
Jacques Calitz
James Croston
Date
Date
30/06/2020
14/08/2020
Checker
Zone 4 (Digested sludge holding tanks)
IED CIRIA 736 Risk Assessment
James Croston
Approver
Date
Note on J17: Calitz, Jacques: Add manually. Based on highest risk rating
Note on F61: Calitz, Jacques: Add manually. Based on highest risk rating
Note on J61: Calitz, Jacques: Add manually. Based on highest risk rating
Note on C90: Calitz, Jacques: Add manually. Based on highest risk rating

## Mitigation
Catastrophic failure - modes (loss of containment) - pragmatic solution
Risk | Cause | Existing consequence and mitigation measure | Existing zone risk rating | Proposed Mitigation | Risk rating after mitigation
| Operational failure - tank (partial) | Each digester spills 80 - 100m3 of digestate to the digested sludge holding tanks each day. The filling of the zones is controlled manually by operational staff. Zones are filled on a zone by zone basis. Based on the digester feed pumps, the gravity flow rate to the digested sludge holding tanks would be 8-10l/s (4-5l/s per digester feed pump). Operational staff have not reported any cases of overflows and both tanks are covered. Both tanks have high level overflows, but based on discussions with operational staff, the overflows are not in operation and valves are closed. The level within the tanks are monitored by ultrasonic level sensors, but not linked to Scada or alarmed. In the unlikely event if there is an overflow, the volume lost would be minimal (assumed <29m3 based on hourly flow rate to holding tanks). As currently filling is done manually, spills would be limited to a low volume as valves can be shut with relative ease by operational staff filling the tanks. Each tank is filled individually. Total loss of containment is not credible when considering overflowing or foaming of the tank (partial loss of containment would be more likely to occur but is still very unlikely). | M | In the case that tank overflows due to overfilling, spillage can be controlled by operators as the tanks are filled manually and spillage volume would be minimal. No cases were reported by the operational team. In the unlikely event that the an overflow does occur, sludge will cascade towards the road to the north and eventually the humus tanks. Ther is potential for sludge to infiltrate into the ground around tank or cascade into the drainage network (liquor return). To avoid any overfilling/overflow from all of the tanks, the existing ultrasonic depth meters need the necessary telemetry controls and alarming. Filling of the tanks should also be automated or have safeguards that inhibit the feed pumps on high high level. In the case high level overflows or automated control are not incorporated, secondary containment should be provided for the possible overfilling volume. It was assumed that 1 hour of the max flow from the digester (10l/s) could be lost before operational staff would shut off the valve (36m3). Only competent and trained staff operate the site. The zone is robust and safe provided the permeable areas around the digested sludge holding tanks (grassed areas) is replaced with impermeable hardstanding to remove the pathway to the ground and containment is provided to contain the overflow/overfilling volume within the site. | L
| Structural failure - tank (catastrophic) | Tanks are located above ground. In the case of significant damage above ground, the total volume contained above ground could be lost. It is however very unlikely for the tanks to fail catastrophically structurally as the tanks are fit for purpose. Sludge could be lost if the seal and connection between the tank and slab fails catastrophically. There have been cases in the past where the total above ground volume was lost through the base of the tank when the seal failed. GFS tanks have in the past also had the pipe connections to the tank fail (mixer connection), causing a rupture/hole in the tank, through which the total inventory is lost. The existing high level overflow connecting pipework is located at ground level, the tank could potentially lose its total above ground volume through the hole if the pipework were to break off the tank (very unlikely). There are no credible scenarios that could lead to a catastrophic failure of the digesters (partial loss of containment would be more likely to occur but still very unlikely). | M | Original tank construction was GFS (2003). Operational staff stated that there have been no known visible leaks from the tanks and no external damage or significant corrosion. Construction was fit for purpose at the time of construction. If catastrophic failure of the tank occurs, 468m3 could potentially be lost above ground (through bottom of tank or pipe connection). Due to the very unlikely event of catastrophic failure of the tank caused by operational or maintenance procedures (excessive external damage or pipe connection failing) or seal at tank base failing, total loss of containment is very unlikely. If damage does occur or seal leakage is excessive, operational staff can isolate the tank and drain it down quickly reducing the loss of containment. In the unlikely event that tank loses containment above ground through structural failure, the sludge will cascade towards the road to the north and eventually the humus tanks. There is potetnial for sludge to infiltrate into the ground around tank or cascade into the drainage network (liquor return). As catastrophic failure of the total volume is very unlikely, to allow for some loss of containment due to catastrophic failure or significant mixer connection leakage (pre-failure), secondary containment to allow for minimum of 500mm of digester height volume loss until tank is drained down by operational staff (during operating hours). Allow for a loss of sludge volume equivalent to 500mm drop in level in the digested sludge holding tank. This allows for time required for operators to respond and drain the affected tank down. In the case of valve seizure (double jeopardy) or when staff are not on site - Allow for an additional 500mm of volume loss (1000mm in total). To reduce the likelihood of loss of containment, the tanks should be structurally inspected on an annual basis by a competent engineer. The tanks should then be refurbished if necessary. Ultrasonic meters in tanks should be alarmed if there is a significant and unanticipated drop in level to mitigate any significant loss of containment. The zone is robust and safe provided the permeable areas around the digested sludge holding tanks (grassed areas) is replaced with impermeable hardstanding to remove the pathway to the ground. | L
| Structural failure - tank (partial) | Tanks are located above ground. Any significant loss of containment, would spill above ground. Structural failure of the tank would mainly be through corrosion (bolts, connections between panels). In the case of significant corrosion and leaks forming above ground, the volume contained above ground would seep through the leaks. The tank could potentially lose the above ground volume over a long period of time (very unlikely). Due to operational presence on site, large drops in levels in the tanks and significant leaks above ground would be noticed. Significant corrosion below/above ground would also be easily spotted if tank is inspected. There are no credible scenarios that could lead to a catastrophic failure of the digesters (partial loss of containment would be more likely to occur but still very unlikely). | M | Original tank construction was GFS (drawings state 1980, but operations state that it was constructed in 2003). Operational staff stated that there have been no known visible leaks from the tanks and no external damage or significant corrosion. Construction was fit for purpose at the time of construction. In the event that tank loses containment above or below ground through structural failure (corrosion/leaks), sludge would weep through the leaks at a very slow rate. The volume would slowly flow down the side of the tank and gather around the tank. Significant corrosion and the subsequent leaks (especially above ground) would be spotted by operations during their daily inspections and the tank would be isolated and drained down until repaired if the corrosion and leak is significant. Secondary containment is thus not proposed and loss of containment volume is assumed will be able to be accommodated in the hardstanding area around the tank and in the drainage system. In the unlikely event that tank loses containment above ground through structural failure, based on topography, sludge will cascade towards the road to the north and eventually the humus tanks. Potential to infiltrate into the ground around tank or cascade into the drainage network (liquor return). To reduce the likelihood of loss of containment, the tanks should be structurally inspected on an annual basis by a competent engineer. The tanks should then be refurbished if necessary. Ultrasonic meters in tanks should be alarmed if there is a significant and unanticipated drop in level to mitigate any significant loss of containment. The zone is robust and safe provided the permeable areas around the digested sludge holding tanks (grassed areas) is replaced with impermeable hardstanding to remove the pathway to the ground and secondary containment is provided to contain the potential volume loss of the digested sludge holding tank within the site. Associated drainage would connect to the liquor return drainage system. The tanks should be inspected on at least an annual basis by a competent engineer in addition to the current maintenance strategy. This can be undertaken during the sludge plant's annual maintenance and inspection shutdown. No further mitigation is considered to be necessary. | L
| Structural failure - pipework (catastrophic) | In the extremely unlikely event where the above ground pipework or valves in the chambers fail completely. A significant volume could be lost if the valves are not closed by operational staff or tanks are not drained down to limit loss of containment. As the site is generally manned, valves would be closed and operated by operational staff if the pipes were to fail. In the case where critical pipework fails and valves cannot mitigate the spillage, the tank could lose its full volume. There are no credible scenarios that could lead to a catastrophic failure of the pipework (partial loss of containment would be more likely to occur but still very unlikely). | M | In the unlikely event where the above ground pipework or valves in the chambers fail completely. a significant volume could be lost if the valves are not closed by operational staff or tanks are not drained down to limit loss of containment. As complete loss of containment is unlikely, it is proposed that the volume contained in the above ground pipe length would need to be contained. As the site is generally manned, valves would be closed and operated by operational staff if the pipes were to fail. Secondary containment is not proposed and volume is assumed will be able to be accommodated in the hardstanding area around the tank and pipework and in the drainage system. The zone is robust and safe provided the permeable areas around the digested sludge holding tanks (grassed areas) is replaced with impermeable hardstanding to remove the pathway to the ground and secondary containment is provided to contain the potential volume loss of the digested sludge holding tank within the site. Associated drainage would connect to the liquor return drainage system. The above ground pipework should continue to be regularly inspected during daily and weekly inspections to enable proactive maintenance when required. Below ground pipework and chambers should be inspected on an annual basis to check their integrity (CCTV and the necessary leakage detection via falling head tests). | L
| Structural failure - pipework (partial) | Majority of pipework, connections and chambers are located below ground (cast and ductile iron). Some of the connecting pipework is located above ground. If loss of containment occurs underground, sludge will percolate into the soil at a slow rate over a long period. If significant leaks, localised wet areas will be present above ground. If loss of containment occurs above ground through leaks or damage to pipework, due to the permeable grass around tank, sludge will also percolate into the soil at a slow rate over a long period. Due to operational presence on site, significant leaks (above or below) ground would be noticed and loss of containment would be mitigated through operational measures (closing of valves). No significant leaks were mentioned by operational staff. Total loss of containment is therefore not deemed to be a credible scenario. Partial loss of containment is possible but still highly unlikely when considering larger volumes. | M | Original construction was ductile and cast iron (1981). Operational staff stated that there has been no known visible leaks on site. As construction was fit for purpose at the time of construction, secondary containment provision is not considered for the underground pipework. Based on experience the volume that could be lost due to above ground pipework leaks is minimal. Significant leaks would be spotted by operational staff during their daily inspection (site is also manned during the day) and repaired and any loss of containment mitigated. The volume lost to leaks would be able to be contained in the new hardstanding area around the tanks (replacing the stone areas) and drainage pipework. No secondary containment required. Sludge would seep through the leaks at a very slow rate. The volume would slowly flow down the side of the pipe and gather around the pipework. The actual volume lost would be minimal. In the unlikely event that there is significant loss of containment through pipework above ground, based on topography and the type of inventory, loss of containment would be limited to the new and existing hardstanding area around the pipework and tanks. The zone is robust and safe provided the permeable areas around the digested sludge holding tanks (grassed areas) is replaced with impermeable hardstanding to remove the pathway to the ground and secondary containment is provided to contain the potential volume loss of the digested sludge holding tank within the site. Associated drainage would connect to the liquor return drainage system. The above ground pipework should continue to be regularly inspected during daily and weekly inspections to enable proactive maintenance when required. Below ground pipework and chambers should be inspected on an annual basis to check their integrity (CCTV and the necessary leakage detection via falling head tests). | L
| Vehicular impact (partial to catastrophic) | No known vehicle impacts - but no barrier/protection Vehicles could potentially impact and damage GFS tank which is located above ground. Vehicular impact could cause Significant damage to the tank causing the total volume to be lost. The GFS tanks would not be able to sustain a horizontal impact especially high speed collisions. Vehicles are however unlikely to impact the tanks due to their location. Total loss of containment is therefore not deemed to be a credible scenario. | M | Total loss of containment could occur if the vehicle impact causes significant damage to the tank. High speed impact unlikely, but vehicle could damage pipework connected to tank or the tank itself. Vehicle barriers or bollards are proposed around front of the tanks along the road to mitigate any potential impacts from vehicles and potential damage which could lead to loss of containment. | L
| Vandalism | No known vandalism to tanks or pipework - CCTV cameras on site. Thefts in the past based on comments from operators but not damage to any of the assets on site. If vandalism damage were to occur, total loss of containment is unlikely. Partial loss of containment would be more likely to occur if slight damage was done. | M | Vandalism on site has been mainly theft. If pipes and tanks get damaged, because it is operated on a daily basis with operational staff present, the risk of loss of containment is low. If there are any signs of damage due to vandalism operators will fix any damage first. No mitigation measures proposed, existing measures deemed adequate. | L
| Flooding | No flooding has been reported/recorded by the operators Even if flooding occurred, tanks will not be damaged and full volume of sludge will not be lost. There could be a potential for the flood water to be contaminated. The flood water could enter the below ground chambers around the tanks and potentially get contaminated. | M | Even if flooding occurred, tanks will not be damaged and full volume of sludge will not be lost. There could be a potential for the flood water to be contaminated when entering chambers, but only if there is a loss of containment. No mitigation measures proposed, existing measures deemed adequate. | L
The probability and risk of failure from the tanks is low and any associated loss of inventory volume would be contained within the new adjacent hardstanding area. In line with CIRIA 736, the grassed areas should be replaced with impermeable hardstanding and containment needs to be provided if the digested sludge holding tank had significant leaks. The site maintenance strategy and annual plant shutdown does need to include structural assessments of the containment structures, including the surrounding hardstanding areas. Drainage pipework and above ground process pipework should be inspected by a competent engineer to allow for pro-active maintenance.
14/08/2020
File Ref
Version
B14411-123532-ZZ-XX-AS-ZA-CI1005
P01
Originator
Jacques Calitz
James Croston
Date
Date
30/06/2020
14/08/2020
Checker
Zone 4 (Digested sludge holding tanks)
IED CIRIA 736 Risk Assessment
James Croston
Approver
Date

## Containment volume - Total vol.
Secondary containment volume requirement - Inventory volume (above ground)
Digested sludge holding tank 1 | 468 | m3 | (Inventory volume - above ground below overflow)
Digested sludge holding tank 2 | 468 | m3 | (Inventory volume - above ground below overflow)
Total volume | 936 | m3
110% and 25% rules (CIRIA 736)
*110% of largest tank | 514.8 | m3
25% of total tank volume | 234 | m3
Secondary storage to be provided | 514.8 | m3
*Note that 10% includes for rainfall and is the minimum allowable storage that can be provided
Estimate of area required - local containment (100% of volume)
Volume 100% (m3) | Height of containment (m) | Area based on flat ground (m2)
514.8 | 100 | 5148
514.8 | 200 | 2574
514.8 | 300 | 1716
514.8 | 400 | 1287
514.8 | 500 | 1029.6
514.8 | 600 | 858
514.8 | 700 | 735.4286
514.8 | 800 | 643.5
514.8 | 900 | 572
514.8 | 1000 | 514.8
514.8 | 1100 | 468
514.8 | 1200 | 429
514.8 | 1300 | 396
514.8 | 1400 | 367.7143
514.8 | 1500 | 343.2
514.8 | 1600 | 321.75
514.8 | 1700 | 302.8235
514.8 | 1800 | 286
514.8 | 1900 | 270.9474
514.8 | 2000 | 257.4
Secondary containment volume requirement - Rainfall volume
Area of containment | 500 | m2 | (Area of containment)
24 hour - 1:10 year rainfall | 41 | mm
8 day - 1:10 year rainfall | 95 | mm
Total rainfall volume | 68 | m3
Secondary containment including rainfall |  | 536 | m3
Total secondary containment volume
Volume | 536 | m3
Loss of containment - Time to empty fully
Rate of flow from tank:
Tank volume |  |  | 468 | m3
Diameter of pipe (d) |  |  | 0.25 | m
Area |  |  | 0.049087 | m2
Discharge coefficient (Cd) |  |  | 0.61
Gravitational acceleration (g) |  |  | 9.81 | m/s2
Height within digester tank (H) | Flow rate (Q) m3/s | Diameter of digester (m) | Volume in tank (m3) - above ground | % volume lost | Time to drop in level (min) | Time to empty (cumulative) - min
3.56 | 0.25025 | 15 | 629.1039 | -34.42% |  | 0
3.5 | 0.24813 | 15 | 618.5011 | -32.16% | 0.70615 | 0.70615
3 | 0.22973 | 15 | 530.1438 | -13.28% | 5.9348 | 6.641
2.5 | 0.20971 | 15 | 441.7865 | 5.601% | 6.4103 | 13.0513
2 | 0.18757 | 15 | 353.4292 | 24.48% | 7.0222 | 20.0735
1.5 | 0.16244 | 15 | 265.0719 | 43.36% | 7.851 | 27.9245
1 | 0.13263 | 15 | 176.7146 | 62.24% | 9.0656 | 36.9901
0.5 | 0.093785 | 15 | 88.3573 | 81.12% | 11.103 | 48.0932
0 | 0 | 15 | 0 | 100% | 15.7021 | 63.7952 | Minutes to empty to ground level
14/08/2020
File Ref
Version
B14411-123532-ZZ-XX-AS-ZA-CI1005
P01
Originator
Jacques Calitz
James Croston
Date
Date
30/06/2020
14/08/2020
Checker
Zone 4 (Digested sludge holding tanks)
IED CIRIA 736 Risk Assessment
James Croston
Approver
Date

## Containment - Pragmatic
Secondary containment volume requirement - Inventory volume (above ground)
The most probable failure of the tank, based on experience, is assumed to be through leaks from corrosion or through the base of the tank (sealant failure), causing it to lose a proportion of its total volume and in worst case scenario all its above ground volume. Due to the very unlikely event of catastrophic failure of the tank, causing total loss of containment, the secondary containment volume was based on the worst case between the overfilling volume (most likely) and the loss from the GFS tank through significant leaks (1000mm of tank height). The height of volume loss is lower than the digester due to possible foaming in the digester.
Above ground volume - containment to be provided
Catastrophic failure | 468 | m3
Overfilling volume (1 hours) | 36 | m3
500mm height loss of tank | 66.3661 | m3
1000mm height loss of tank | 132.7323 | m3
15% of tank above ground | 70.2 | m3
Pragmatic volume | 132.7323 | m3
Estimate of area required - local containment (proportion of volume)
Volume loss | Height of containment (mm) | Area based on flat ground (m2)
146.0055 | 100 | 1460.0552
146.0055 | 200 | 730.0276
146.0055 | 300 | 486.6851
146.0055 | 400 | 365.0138
146.0055 | 500 | 292.011
146.0055 | 600 | 243.3425
146.0055 | 700 | 208.5793
146.0055 | 800 | 182.5069
146.0055 | 900 | 162.2284
146.0055 | 1000 | 146.0055
146.0055 | 1100 | 132.7323
146.0055 | 1200 | 121.6713
146.0055 | 1300 | 112.3119
146.0055 | 1400 | 104.2897
146.0055 | 1500 | 97.337
146.0055 | 1600 | 91.2534
146.0055 | 1700 | 85.8856
146.0055 | 1800 | 81.1142
146.0055 | 1900 | 76.845
146.0055 | 2000 | 73.0028
14/08/2020
File Ref
Version
B14411-123532-ZZ-XX-AS-ZA-CI1005
P01
Originator
Jacques Calitz
James Croston
Date
Date
30/06/2020
14/08/2020
Checker
Zone 4 (Digested sludge holding tanks)
IED CIRIA 736 Risk Assessment
James Croston
Approver
Date

## Containment type
Containment to be provided
Based on a Moderate site risk rating for the zone, Class 2 containment is required.
Catastrophic failure
Catastrophic failure assumes the tank loses all its above ground volume and that the total volume would need to be contained.
Material type of containment to be provided
Type | Applicability
Reinforced concrete/masonry flooring and bund | Due to relatively large volume from loss of containment, use of a masonry/concrete bund is generally not appropriate for local containment in this scenario. Due to the limited space available around the area, the use of masonry/concrete bunds is however applicable
Earth banked basins, bunds and flooring | Soil within site is of permeable nature - Clay or impermeable soil type not plentiful Potential for stabilised soil (lime and cement used to make it impermeable) for bund construction. Area of which bunding can be provided is however limited - assuming for example a bund height of 300mm, crest width of 100m, side slopes of 1:3 - a base width of the bund of at least 2000mm is required. Dependant on area required and nature of surrounding area, might be applicable Not applicable within the import sludge tank area.
Containment tank | Nature of catastrophic failure and type of primary containment makes use of a containment tank not appropriate
Type of containment to be provided
Options considered:
Option 1: Local containment (containment for the sludge spillage around the tanks only)
Volume is proposed to be contained within the surrounding area. Where currently permeable (grass), to be made impermeable - concrete surface. Volume is proposed to be contained in new hardstanding area around the tanks. Masonry/concrete bund wall to be constructed.
Option 2: Combination of local and remote (containment for multiple zones)
All sludge processing tanks to be contained within a central bunded area which will allow for lower height bunds around local areas of loss of containment. Where low points are present, area to be raised through speed humps (100mm), kerbs (100mm) or where higher containment heights required via earth bunds (where space permits) or concrete/masonry walls/bunds.
Freeboard allowance
Due to small flow from loss of containment, wave action, which could potentially overtop the bund, not accounted for. No freeboard allowance thus included,
Type of drainage to be provided
Volume is proposed to be contained within bund with no connection to downstream drainage. All existing drainage to be removed. Mobile pumps to be used to remove volume from bund from low point. Daily operational inspection to ensure any rainfall runoff within the bund is removed.
14/08/2020
File Ref
Version
B14411-123532-ZZ-XX-AS-ZA-CI1005
P01
Originator
Jacques Calitz
James Croston
Date
Date
30/06/2020
14/08/2020
Checker
Zone 4 (Digested sludge holding tanks)
IED CIRIA 736 Risk Assessment
James Croston
Approver
Date

## List
Possible Combination |  |  |  | Site Hazard Rating | LLL | MLL | HLL
L | L | L | LLL | L | LLM | MLM | HLM
M | M | L | MML | L | LLH | MLH | HLH
M | L | L | MLL | L | LMM | MMM | HMM
H | L | L | HLL | L | LML | MML | HML
M | M | M | MMM | M | LMH | MMH | HMH
H | M | L | HML | M | LHL | MHL | HHL
H | H | L | HHL | M | LHM | MHM | HHM
H | M | M | HMM | H | LHH | MHH | HHH
H | H | M | HHM | H
H | H | H | HHH | H
< 1 in 100 |  |  | H
1 in 100 to 1 in 1 Million |  |  | M
> 1 in 1 Million |  |  | L
H | H | HH | High
H | M | HM | High
M | H | MH | High
M | M | MM | Moderate
H | L | HL | Moderate
L | H | LH | Moderate
L | L | LL | Low
M | L | ML | Low
L | M | LM | Low
Low |  | Class 1
Moderate |  | Class 2
High |  | Class 3