## Current asset evaluation
Zone 6 - Digested sludge tanks
Description | Digestate is pumped for the digesters to the digested sludge tanks. Sludge enters the tanks from the top of the tank and sludge is then returned to the centrifuge feed tank from the bottom of the tank.
Number of tanks | 3 operational (1 abandoned)
Volume of tank | 950m3 (open tank) - (approximately) - total volume for each tank 100m3 above ground (volume below high level) 175m3 above ground (volume above high level) 675m3 below ground Based on discussions, there is no overflow in place for high levels within the tank.
Material of tank | Concrete
Above/below ground? | Tanks are mostly below ground with a proportion above ground
Pipe material | Connecting pipework assumed to be ductile iron – above and below ground pipes.
Drainage for zone | Road around tanks is assumed to drain via gullies to liquors return tank Grassed area surrounding tank infiltrates into ground
Year of construction | Drawings state 1980
Surrounding area | Surrounding external area is primarily grass - permeable Road around tanks is tarmac - impermeable
Is asset fit for purpose? | The tanks were originally designed and constructed as aeration tanks. Having been converted to sludge holding tanks, they can still contain sludge based on how they were designed. They have been operating with no notable concerns. Tanks have undergone a change of use but still fit for purpose.
Condition of the tank Any tank failures - cracks, flaking, corrosion, overflows, overfilling? | No issues noted from operations. There is however a lot of vegetation growth within the tanks. Known to block the outlet due to crust build-up. The tanks has overflown in the past but not recently.
Condition of pipework Pipe leaks, corrosion? | No visible issues/leaks reported by operational staff Overland pipework temporary - due to crust build up in the 2nd zone
Protection of assets - bollards? | No vehicle impact protection
Control/monitoring/alarming measures in place? | No control measures - tanks are manually filled by operations on a day to day basis. No telemetry or alarms
Secondary containment provided? | None
Secondary containment condition? | N/A
Crust build-up
14/08/2020
File Ref
Version
B14411-123532-ZZ-XX-AS-ZA-CI1007
P01
Originator
Jacques Calitz
James Croston
Date
Date
30/06/2020
14/08/2020
Checker
Zone 6 (Digested sludge holding tanks)
IED CIRIA 736 Risk Assessment
James Croston
Approver
Date

## Zone 6 volume
Volume - open tank |  |  | Length
Length | Area |  | 28000
28 | 33.8 | 946.4
946.4
Volume - open tank (below ground)
Length | Area
28 | 24 | 672
672
Volume - open tank (below overflow above ground)
Length | Area
28 | 3.54 | 99.12
99.12
Volume - open tank (above overflow)
Length | Area
28 | 6.2 | 173.6
173.6
14/08/2020
File Ref
Version
B14411-123532-ZZ-XX-AS-ZA-CI1007
P01
Originator
Jacques Calitz
James Croston
Date
Date
30/06/2020
14/08/2020
Checker
Zone 6 (Digested sludge holding tanks)
IED CIRIA 736 Risk Assessment
James Croston
Approver
Date
Operational top level - 7.12m AOD

## Risk assessment
Source
Material | Physical properties | Maximum quantity | units | Storage | Flammability | Corrosive | Ecotoxicity (based on LD and quantity) | Hazard rating
Digested sludge tank 1 | Liquid with sludge <= 4-5% (digestate) | 950m3 (open tank) - (approximately) - total volume for each tank 100m3 above ground (volume below high level) 175m3 above ground (volume above high level) 675m3 below ground | m3 | Concrete below ground tank with a proportion above ground (not covered) | Not flammable | Possibly | Organic heavy - Nitrogen, Phosphorous, Ammonia, BOD, TSS, COD - Environmental hazard (algae blooms and death of organisms) Pathogens - Human hazard (E.coli etc.) | M
Digested sludge tank 2 | Liquid with sludge <= 4-5% (digestate) | 950m3 (open tank) - (approximately) - total volume for each tank 100m3 above ground (volume below high level) 175m3 above ground (volume above high level) 675m3 below ground | m3 | Concrete below ground tank with a proportion above ground (not covered) | Not flammable | Possibly | Organic heavy - Nitrogen, Phosphorous, Ammonia, BOD, TSS, COD - Environmental hazard (algae blooms and death of organisms) Pathogens - Human hazard (E.coli etc.) | M
Digested sludge tank 3 | Liquid with sludge <= 4-5% (digestate) | 950m3 (open tank) - (approximately) - total volume for each tank 100m3 above ground (volume below high level) 175m3 above ground (volume above high level) 675m3 below ground | m3 | Concrete below ground tank with a proportion above ground (not covered) | Not flammable | Possibly | Organic heavy - Nitrogen, Phosphorous, Ammonia, BOD, TSS, COD - Environmental hazard (algae blooms and death of organisms) Pathogens - Human hazard (E.coli etc.) | M
Digested sludge tank 4 (not in operation) | Not in use | 950m3 (open tank) - (approximately) - total volume for each tank 100m3 above ground (volume below high level) 175m3 above ground (volume above high level) 675m3 below ground | m3 | Concrete below ground tank with a proportion above ground (not covered) | Not flammable | Possibly | Organic heavy - Nitrogen, Phosphorous, Ammonia, BOD, TSS, COD - Environmental hazard (algae blooms and death of organisms) Pathogens - Human hazard (E.coli etc.) | M
Rainwater run-off contaminated by inventory | Surface water mixed with sludge/pollutants | Dependent on area of containment | m3 | N/A | Not flammable | No | Lower concentration of sludge contaminants | L
[7 empty] | Overall | M
Pathway and Receptor
Pathway - the route from primary containment to receptor (extent of loss of containment) |  | Time of concentration/ duration of source outside containment |  | Hazard - Transport potential |  |  | Receptor | Hazard - Damage potential
Tanks are surrounded by permeable grass. Based on available ground information, soil is permeable (infiltration rate of 4 x 10-5m/s) Permeable sub-soils/strata will thus act as a pathway |  | Direct contamination but over an extended period of time |  | M |  |  | Groundwater (underlain by a secondary aquifer) - contaminated through percolation through soil or through fluctuating tidal groundwater level Over a very long period, can contaminate river Dee through groundwater base flow underground | M
If permeable area get saturated (high groundwater) or becomes blocked with sludge, areas will act as impermeable and transport sludge downstream. |  | Direct contamination but over an extended period of time |  | M
Tidally fluctuating groundwater |  | Direct contamination but over an extended period of time |  | M
Existing underground services - ductwork, tunnels etc. (locations not known) |  | Direct contamination but over an extended period of time |  | L
Existing underground sludge pipework |  | Direct contamination but over an extended period of time |  | M
There is impermeable tarmac road surfacing around the tanks. If inventory is cascaded onto road (saturated permeable ground), sludge is assumed will be transported downstream along the road surface into the road gullies and into the site drainage system (liquor return) |  | Minutes - hours |  | H |  |  | WWTW - liquor return tank pumps liquor back to head of works | M
*Flood water - Site is within flood zone 3 (operational staff did however mention no flooding has been recorded within the site) |  | Minutes - N/A (dependant on flooding extent) |  | L |  |  | River Dee - animals and fish (270m away) | H
|  | Overall |  | M |  |  | Overall | M
*Flooding in flood zone 3 only have a 1 in 100 year probability of happening in a year
Combination of Hazards | MMM
Overall risk rating for zone (Ciria 736) | M
Frequency of loss of containment
Failure mode | Description | Existing consequence and mitigation measure | [6 empty] | Annual probability of loss of containment | Rating
Operational failure - tank | Overfilling/overflow of tank | Each digester spills 80 - 100m3 of digestate to the digested sludge holding tanks each day. The filling of the zones is controlled manually by operational staff. Zones are filled on a zone by zone basis. Based on the digester feed pumps, the gravity flow rate to the digested sludge holding tanks would be 8-10l/s (4-5l/s per pump). Operational staff reported that there have been overfilling/overflow cases, but in the past and not recently. Based on discussions with operational staff, there are no high level overflows within the tanks. There are however ultrasonic depth monitors. The level within the tanks are monitored by ultrasonic level sensors, but not linked to Scada or alarmed. In the event if there is an overflow, the volume lost, would be minimal (assumed <29m3 based on hourly flow rate to holding tanks). As currently filling is done manually, spills would be limited to a low volume as valves can be shut with relative ease by operational staff filling the tanks. Each tank is filled individually. Total loss of containment is unlikely (partial loss of containment would be more likely to occur but unlikely) | [6 empty] | 1 in 100 to 1 in 1 Million | M
Structural failure - tank (catastrophic) | Catastrophic failure due to significant external damage | Tanks are primarily located below ground, any loss of containment will be contained primarily underground. The sludge liquid will percolate into the permeable soil at a slow rate over a long period. In the case of significant damage above ground, the total volume contained above ground could be lost. It is however very unlikely for the tanks to fail catastrophically structurally as the tanks are fit for purpose. Total loss of containment could occur. | [6 empty] | < 1 in 1 Million | L
Structural failure - tank (partial) | Most likely through cracks formed in concrete Most critical cracks would be large cracks at low level along the side of the tank walls or tank base. Cracks would need to be large >6mm to allow for sludge to pass through the crack freely. General screens at WwTW are 6-10mm, thus cracks would need to be in the same range to allow for sludge to pass freely. | Tanks are primarily located below ground, any loss of containment, most likely to be due to large cracks, will be contained underground. The sludge liquid will percolate into the permeable soil at a slow rate over a long period. Structural failure of the tank would mainly be through cracks. In the case of significant cracks forming above ground, the volume contained above ground would seep through the cracks. If the cracks are significant (>6mm), the tank could potentially lose the above ground volume over a long period of time (very unlikely). Due to operational presence on site, large drops in levels in the tanks and significant leaks above ground would be noticed. Significant cracks (>6mm) below/above ground would also be easily spotted if tank is inspected. Pipe connections into the tank are at high level and failure of these connections would not cause significant loss of containment. Total loss of containment is unlikely (partial loss of containment would be more likely to occur, but over a long period) | [6 empty] | < 1 in 1 Million | L
Structural failure - pipework (catastrophic) | Loss of containment due to failure of above ground connecting pipework | In the unlikely event where the above ground pipework or valves in the chambers fail completely. A significant volume could be lost if the valves are not closed by operational staff or tanks are not drained down to limit loss of containment. As the site is generally manned, valves would be closed and operated by operational staff if the pipes were to fail. In the case where critical pipework fails and valves cannot mitigate the spillage, the tank could lose its full volume. Total loss of containment could occur but unlikely | [6 empty] | < 1 in 1 Million | L
Structural failure - pipework (partial) | Loss of containment most likely to occur where there are weak points in the pipework - Most likely through failures where pipe connects with the structure, bolts/sealant at pipe flanges/valves or along any pipe pitting. Weak point could be created through either human damage (during maintenance/operation), erosion (high velocities and silt content within the pipe) or environmental (corrosion) | Majority of pipework, connections and chambers are located below ground (cast and ductile iron). Some of the connecting pipework is located above ground. If loss of containment occurs underground, sludge will percolate into the soil at a slow rate over a long period. If significant leaks, localised wet areas will be present above ground. If loss of containment occurs above ground through leaks or damage to pipework, due to the permeable grass around tank, sludge will also percolate into the soil at a slow rate over a long period. In the unlikely event where the above ground pipework fails (connecting pipework), the total above ground volume of the tank could be lost if operation is unmanned. Due to operational presence on site, significant leaks (above or below) ground would be noticed and loss of containment would be mitigated through operational measures (closing of valves). No significant leaks were mentioned by operational staff. Total loss of containment could occur but unlikely | [6 empty] | < 1 in 1 Million | L
Vehicular impact | Impact from vehicles - damage to pipes or tank causing loss of containment | No known vehicle impacts - but no barrier/protection Vehicles could potentially impact and damage the portion of the concrete tank which is located above ground. Vehicles are however unlikely to cause significant damage. | [6 empty] | 1 in 100 to 1 in 1 Million | M
Vandalism | Vandalism of infrastructure - damage to pipes or tank causing loss of containment | No known vandalism to tanks or pipework - CCTV cameras on site. Thefts in the past based on comments from operators but not damage to any of the assets on site. If vandalism damage were to occur, total loss of containment is unlikely. Partial loss of containment would be more likely to occur if slight damage was done. | [6 empty] | < 1 in 1 Million | L
Flooding | River flooding - Flood zone 3 - - damage to pipes or tank causing loss of containment | No flooding has been reported/recorded by the operators Even if flooding occurred, tanks will not be damaged and full volume of sludge will not be lost. There could be a potential for the flood water to be contaminated. The flood water could enter the below ground chambers around the tanks and potentially get contaminated. | [6 empty] | < 1 in 1 Million | L
*Site is manned. Probability and frequency thus reduced
Frequency of loss of containment (Ciria 736) | M
Overall zone hazard rating
Overall zone hazard rating (Ciria 736) | Moderate
Containment required
Containment required | Class 2
Road gullies
Permeable ground
Road gullies
Overland flow paths
250m
170m
270m
River Dee
Liquor return at head of works
3rd party land
Ditch
110m
14/08/2020
File Ref
Version
B14411-123532-ZZ-XX-AS-ZA-CI1007
P01
Originator
Jacques Calitz
James Croston
Date
Date
30/06/2020
14/08/2020
Checker
Zone 6 (Digested sludge holding tanks)
IED CIRIA 736 Risk Assessment
James Croston
Approver
Date
Note on J20: Calitz, Jacques: Add manually. Based on highest risk rating
Note on F67: Calitz, Jacques: Add manually. Based on highest risk rating
Note on J67: Calitz, Jacques: Add manually. Based on highest risk rating
Note on C96: Calitz, Jacques: Add manually. Based on highest risk rating

## Mitigation
Catastrophic failure - modes (loss of containment) - pragmatic solution
Risk | Cause | Existing consequence and mitigation measure | Existing zone risk rating | Proposed Mitigation | Risk rating after mitigation
| Operational failure - tank | Each digester spills 80 - 100m3 of digestate to the digested sludge holding tanks each day. The filling of the zones is controlled manually by operational staff. Zones are filled on a zone by zone basis. Based on the digester feed pumps, the gravity flow rate to the digested sludge holding tanks would be 8-10l/s (4-5l/s per pump). Operational staff reported that there have been overfilling/overflow cases, but in the past and not recently. Based on discussions with operational staff, there are no high level overflows within the tanks. There are however ultrasonic depth monitors. The level within the tanks are monitored by ultrasonic level sensors, but not linked to Scada or alarmed. In the event if there is an overflow, the volume lost, would be minimal (assumed <29m3 based on hourly flow rate to holding tanks). As currently filling is done manually, spills would be limited to a low volume as valves can be shut with relative ease by operational staff filling the tanks. Each tank is filled individually. Total loss of containment is unlikely (partial loss of containment would be more likely to occur but unlikely) | M | In the case that tank overflows, spillage can be controlled by operators as the tanks are filled manually and spillage volume would be minimal. Operational staff have not reported any cases of overflows in the covered old digester tank, but there have been overflows for the uncovered tank. In the unlikely event that tank loses containment, overflows, based on topography, sludge will cascade towards the road. Potential to infiltrate into the ground around tank or cascade into the drainage network (liquor return). To avoid any overfilling/overflow from all of the tanks, the existing ultrasonic depth meters need the necessary telemetry controls and alarming. Filling of the tanks should also be automated. In the case high level overflows or automated control are not incorporated, secondary containment should be provided for the possible overfilling volume. It was assumed that 1 hour of the max flow from the digester (10l/s) could be lost before operational staff would shut off the valve (36m3). Secondary containment is thus not proposed and volume is assumed will be able to be accommodated in the hardstanding area around the tank including the road and in the drainage system. Only competent and trained staff operate the site. The zone is robust and safe provided the permeable areas around the digested sludge holding tanks (grassed/paved areas) is replaced with impermeable hardstanding to remove the pathway to the ground. | L
| Structural failure - tank (catastrophic) | Tanks are primarily located below ground, any loss of containment will be contained primarily underground. The sludge liquid will percolate into the permeable soil at a slow rate over a long period. In the case of significant damage above ground, the total volume contained above ground could be lost. It is however very unlikely for the tanks to fail catastrophically structurally as the tanks are fit for purpose. Total loss of containment could occur. | M | Original tank construction was reinforced concrete (1981). Operational staff stated that there have been no known visible leaks from the tanks. Construction was fit for purpose at the time of construction. If catastrophic failure of the tank occurs, 110m3 could potentially be lost above ground, with 770m3 which can be lost below ground. Due to the very unlikely event of catastrophic failure of the tank caused by operational or maintenance procedures (excessive external damage), total loss of containment is very unlikely. If damage does occur, operational staff can isolate the tank and drain it down quickly reducing the loss of containment. The total above ground volume would also be easily contained within the road surrounding the tank and no secondary containment is required. For the volume located below ground, any loss of containment, will be contained underground. The sludge liquid will percolate into the permeable soil at a slow rate over a long period (4 x 10-5 m/s). Most probably through infiltration through the soil rather than spilling onto surface. In the unlikely event that tank loses containment through structural failure above ground, based on topography, sludge will cascade towards the road. Potential to infiltrate into the ground around tank or cascade into the drainage network (liquor return). To reduce the likelihood of loss of containment, the tanks should be structurally inspected on an annual basis by a competent engineer. The tanks should then be refurbished if necessary. Ultrasonic meters in tanks should be alarmed if there is a significant and unanticipated drop in level to mitigate any significant loss of containment. The zone is robust and safe provided the permeable areas around the digested sludge holding tanks (grassed/paved areas) is replaced with impermeable hardstanding to remove the pathway to the ground. Associated drainage would connect to the liquor return drainage system. The tanks should be inspected on at least an annual basis by a competent engineer in addition to the current maintenance strategy. This can be undertaken during the sludge plant's annual maintenance and inspection shutdown. No further mitigation is considered to be necessary. | L
| Structural failure - tank (partial) | Tanks are primarily located below ground, any loss of containment, most likely to be due to large cracks, will be contained underground. The sludge liquid will percolate into the permeable soil at a slow rate over a long period. Structural failure of the tank would mainly be through cracks. In the case of significant cracks forming above ground, the volume contained above ground would seep through the cracks. If the cracks are significant (>6mm), the tank could potentially lose the above ground volume over a long period of time (very unlikely). Due to operational presence on site, large drops in levels in the tanks and significant leaks above ground would be noticed. Significant cracks (>6mm) below/above ground would also be easily spotted if tank is inspected. Pipe connections into the tank are at high level and failure of these connections would not cause significant loss of containment. Total loss of containment is unlikely (partial loss of containment would be more likely to occur, but over a long period) | M | Original tank construction was reinforced concrete (1981). Operational staff stated that there have been no known visible leaks from the tanks. Construction was fit for purpose at the time of construction. In the event that tank loses containment above or below ground through structural failure (cracks), sludge would weep through the cracks at a very slow rate. The volume would slowly flow down the side of the tank and gather around the tank. Very large cracks and the subsequent leaks (especially above ground) would be spotted by operations during their daily inspections and the tank would be isolated and drained down until repaired if the crack is significant. Secondary containment is thus not proposed and volume is assumed will be able to be accommodated in the hardstanding area around the tank and in the drainage system. In the unlikely event that tank loses significant containment above ground through structural failure (large cracks), based on topography, sludge will cascade towards the road and eventually into the drainage system. Potential to infiltrate into the ground around tank (stone) or cascade into the drainage network (liquor return). To reduce the likelihood of loss of containment, the tanks should be structurally inspected on an annual basis by a competent engineer. The tanks should then be refurbished if necessary. Ultrasonic meters in tanks should be alarmed if there is a significant and unanticipated drop in level to mitigate any significant loss of containment. The zone is robust and safe provided the permeable areas around the digested sludge holding tanks (grassed/paved areas) is replaced with impermeable hardstanding to remove the pathway to the ground. Associated drainage would connect to the liquor return drainage system. The tanks should be inspected on at least an annual basis by a competent engineer in addition to the current maintenance strategy. This can be undertaken during the sludge plant's annual maintenance and inspection shutdown. No further mitigation is considered to be necessary. | L
| Structural failure - pipework (catastrophic) | In the unlikely event where the above ground pipework or valves in the chambers fail completely. A significant volume could be lost if the valves are not closed by operational staff or tanks are not drained down to limit loss of containment. As the site is generally manned, valves would be closed and operated by operational staff if the pipes were to fail. In the case where critical pipework fails and valves cannot mitigate the spillage, the tank could lose its full volume. Total loss of containment could occur but unlikely | M | In the unlikely event where the above ground pipework or valves in the chambers fail completely. a significant volume could be lost if the valves are not closed by operational staff or tanks are not drained down to limit loss of containment. As complete loss of containment is unlikely, it is proposed that the volume contained in the above ground pipe length would need to be contained. As the site is generally manned, valves would be closed and operated by operational staff if the pipes were to fail. Secondary containment is not proposed and volume is assumed will be able to be accommodated in the hardstanding area around the tank and pipework and in the drainage system. The zone is robust and safe provided the permeable areas around the digested sludge holding tanks (grassed/paved areas) is replaced with impermeable hardstanding to remove the pathway to the ground. Associated drainage would connect to the liquor return drainage system. The above ground pipework should continue to be regularly inspected during daily and weekly inspections to enable proactive maintenance when required. Below ground pipework and chambers should be inspected on an annual basis to check their integrity (CCTV and the necessary leakage detection via falling head tests). | L
| Structural failure - pipework (partial) | Majority of pipework, connections and chambers are located below ground (cast and ductile iron). Some of the connecting pipework is located above ground. If loss of containment occurs underground, sludge will percolate into the soil at a slow rate over a long period. If significant leaks, localised wet areas will be present above ground. If loss of containment occurs above ground through leaks or damage to pipework, due to the permeable grass around tank, sludge will also percolate into the soil at a slow rate over a long period. In the unlikely event where the above ground pipework fails (connecting pipework), the total above ground volume of the tank could be lost if operation is unmanned. Due to operational presence on site, significant leaks (above or below) ground would be noticed and loss of containment would be mitigated through operational measures (closing of valves). No significant leaks were mentioned by operational staff. Total loss of containment could occur but unlikely | M | Original construction was ductile and cast iron (1981). Operational staff stated that there has been no known visible leaks on site. As construction was fit for purpose at the time of construction, secondary containment provision is not considered for the underground pipework. Based on experience the volume that could be lost due to above ground pipework leaks is minimal. Significant leaks would be spotted by operational staff during their daily inspection (site is also manned during the day) and repaired and any loss of containment mitigated. The volume lost to leaks would be able to be contained in the new hardstanding area around the tanks (replacing the stone areas) and drainage pipework. No secondary containment required. Sludge would seep through the leaks at a very slow rate. The volume would slowly flow down the side of the pipe and gather around the pipework. The actual volume lost would be minimal. In the unlikely event that there is significant loss of containment through pipework above ground, based on topography and the type of inventory, loss of containment would be limited to the new and existing hardstanding area around the pipework and tanks. The zone is robust and safe provided the permeable areas around the digested sludge holding tanks (grassed/paved areas) is replaced with impermeable hardstanding to remove the pathway to the ground. Associated drainage would connect to the liquor return drainage system. The above ground pipework should continue to be regularly inspected during daily and weekly inspections to enable proactive maintenance when required. Below ground pipework and chambers should be inspected on an annual basis to check their integrity (CCTV and the necessary leakage detection via falling head tests). | L
| Vehicular impact | No known vehicle impacts - but no barrier/protection Vehicles could potentially impact and damage the portion of the concrete tank which is located above ground. Vehicles are however unlikely to cause significant damage. | M | Total loss of containment could occur if the vehicle impact causes significant damage to the tank. High speed impact unlikely, but vehicle could damage pipework connected to tank or the tank itself. No mitigation measures proposed, existing measures deemed adequate. | L
| Vandalism | No known vandalism to tanks or pipework - CCTV cameras on site. Thefts in the past based on comments from operators but not damage to any of the assets on site. If vandalism damage were to occur, total loss of containment is unlikely. Partial loss of containment would be more likely to occur if slight damage was done. | M | Vandalism on site has been mainly theft. If pipes and tanks get damaged, because it is operated on a daily basis with operational staff present, the risk of loss of containment is low. If there are any signs of damage due to vandalism operators will fix any damage first. No mitigation measures proposed, existing measures deemed adequate. | L
| Flooding | No flooding has been reported/recorded by the operators Even if flooding occurred, tanks will not be damaged and full volume of sludge will not be lost. There could be a potential for the flood water to be contaminated. The flood water could enter the below ground chambers around the tanks and potentially get contaminated. | M | Even if flooding occurred, tanks will not be damaged and full volume of sludge will not be lost. There could be a potential for the flood water to be contaminated when entering chambers, but only if there is a loss of containment. No mitigation measures proposed, existing measures deemed adequate. | L
The probability and risk of failure from the tanks is low and any associated loss of inventory volume would be contained within the new adjacent hardstanding area. In line with CIRIA 736, the grassed/paved areas should be replaced with impermeable hardstanding. The site maintenance strategy and annual plant shutdown does need to include structural assessments of the containment structures, including the surrounding hardstanding areas. Drainage pipework and above ground process pipework should be inspected by a competent engineer to allow for pro-active maintenance.
14/08/2020
File Ref
Version
B14411-123532-ZZ-XX-AS-ZA-CI1007
P01
Originator
Jacques Calitz
James Croston
Date
Date
30/06/2020
14/08/2020
Checker
Zone 6 (Digested sludge holding tanks)
IED CIRIA 736 Risk Assessment
James Croston
Approver
Date

## Containment volume - Total vol.
Secondary containment volume requirement - Inventory volume (above ground)
Digested sludge holding tank 1 | 100 | m3 | (Inventory volume - above ground)
Digested sludge holding tank 2 | 100 | m3 | (Inventory volume - above ground)
Digested sludge holding tank 3 | 100 | m3 | (Inventory volume - above ground)
Total volume | 300 | m3
110% and 25% rules (CIRIA 736)
*110% of largest tank | 110 | m3
25% of total tank volume | 75 | m3
Secondary storage to be provided | 110 | m3
*Note that 10% includes for rainfall and is the minimum allowable storage that can be provided
Estimate of area required - local containment (100% of volume)
Volume 100% (m3) | Height of containment (m) | Area based on flat ground (m2)
110 | 100 | 1100
110 | 200 | 550
110 | 300 | 366.6667
110 | 400 | 275
110 | 500 | 220
110 | 600 | 183.3333
110 | 700 | 157.1429
110 | 800 | 137.5
110 | 900 | 122.2222
110 | 1000 | 110
110 | 1100 | 100
110 | 1200 | 91.6667
110 | 1300 | 84.6154
110 | 1400 | 78.5714
110 | 1500 | 73.3333
110 | 1600 | 68.75
110 | 1700 | 64.7059
110 | 1800 | 61.1111
110 | 1900 | 57.8947
110 | 2000 | 55
Secondary containment volume requirement - Rainfall volume
Area of containment | 300 | m2 | (Area of containment)
24 hour - 1:10 year rainfall | 41 | mm
8 day - 1:10 year rainfall | 95 | mm
Total rainfall volume | 40.8 | m3
Secondary containment including rainfall |  | 140.8 | m3
Total secondary containment volume
Volume | 140.8 | m3
Loss of containment - Time to empty fully
Rate of flow from tank:
Tank volume |  |  | 100 | m3
Diameter of pipe (d) |  |  | 0.25 | m
Area |  |  | 0.049087 | m2
Discharge coefficient (Cd) |  |  | 0.61
Gravitational acceleration (g) |  |  | 9.81 | m/s2
Height within digester tank (H) | Flow rate (Q) m3/s | Diameter of digester (m) | Volume in tank (m3) - above ground | % volume lost | Time to drop in level (min) | Time to empty (cumulative) - min
3.56 | 0.25025 | 15 | 629.1039 | -529.1% |  | 0
3.5 | 0.24813 | 15 | 618.5011 | -518.5% | 0.70615 | 0.70615
3 | 0.22973 | 15 | 530.1438 | -430.1% | 5.9348 | 6.641
2.5 | 0.20971 | 15 | 441.7865 | -341.8% | 6.4103 | 13.0513
2 | 0.18757 | 15 | 353.4292 | -253.4% | 7.0222 | 20.0735
1.5 | 0.16244 | 15 | 265.0719 | -165.1% | 7.851 | 27.9245
1 | 0.13263 | 15 | 176.7146 | -76.71% | 9.0656 | 36.9901
0.5 | 0.093785 | 15 | 88.3573 | 11.64% | 11.103 | 48.0932
0 | 0 | 15 | 0 | 100% | 15.7021 | 63.7952 | Minutes to empty to ground level
14/08/2020
File Ref
Version
B14411-123532-ZZ-XX-AS-ZA-CI1007
P01
Originator
Jacques Calitz
James Croston
Date
Date
30/06/2020
14/08/2020
Checker
Zone 6 (Digested sludge holding tanks)
IED CIRIA 736 Risk Assessment
James Croston
Approver
Date

## Containment - Pragmatic
Secondary containment volume requirement - Inventory volume (above ground)
The most probable failure of the tank, based on experience, is assumed to be through operational failure (overfilling) and cracks in the tank, causing it to lose all its above ground volume. Due to the very unlikely event of catastrophic failure of the tank, causing total loss of containment, the secondary containment volume was based on the worst case between the overfilling volume (most likely) and the loss from the concrete tank through significant cracks (leaks). The height of volume loss is lower than the digester due to possible foaming in the digester.
Above ground volume - containment to be provided
Catastrophic failure | 100 | m3
Overfilling volume (1 hours) | 36 | m3
Total above ground volume | 100 | m3
15% of tank above ground | 15 | m3
Pragmatic volume | 100 | m3
Estimate of area required - local containment (proportion of volume)
Volume loss | Height of containment (mm) | Area based on flat ground (m2)
110 | 100 | 1100
110 | 200 | 550
110 | 300 | 366.6667
110 | 400 | 275
110 | 500 | 220
110 | 600 | 183.3333
110 | 700 | 157.1429
110 | 800 | 137.5
110 | 900 | 122.2222
110 | 1000 | 110
110 | 1100 | 100
110 | 1200 | 91.6667
110 | 1300 | 84.6154
110 | 1400 | 78.5714
110 | 1500 | 73.3333
110 | 1600 | 68.75
110 | 1700 | 64.7059
110 | 1800 | 61.1111
110 | 1900 | 57.8947
110 | 2000 | 55
14/08/2020
File Ref
Version
B14411-123532-ZZ-XX-AS-ZA-CI1007
P01
Originator
Jacques Calitz
James Croston
Date
Date
30/06/2020
14/08/2020
Checker
Zone 6 (Digested sludge holding tanks)
IED CIRIA 736 Risk Assessment
James Croston
Approver
Date

## Containment type
Containment to be provided
Based on a Moderate site risk rating for the zone, Class 1 containment is required.
Catastrophic failure
Catastrophic failure assumes the tank loses all its above ground volume and that the total volume would need to be contained.
Material type of containment to be provided
Type | Applicability
Reinforced concrete/masonry flooring and bund | Due to small volume from loss of containment, use of a masonry/concrete bund is appropriate
Earth banked basins, bunds and flooring | Soil within site is of permeable nature - Clay or impermeable soil type not plentiful Potential for stabilised soil (lime and cement used to make it impermeable) for bund construction. Area of which bunding can be provided is however limited - assuming for example a bund height of 300mm, crest width of 100m, side slopes of 1:3 - a base width of the bund of at least 2000mm is required. Dependant on area required and nature of surrounding area, might be applicable Not applicable within the tank area.
Containment tank | Nature of catastrophic failure and type of primary containment makes use of a containment tank not appropriate
Type of containment to be provided
Options considered:
Option 1: Local containment (containment for the spillage around the tanks only)
Volume is proposed to be contained within the surrounding area. Where currently permeable (grassed area), to be made impermeable - concrete surface. Volume is proposed to be contained within the proposed hardstanding around the tanks. Concrete/masonry wall/bund and kerb heights to be increased locally to contain volume.
Option 2: Local containment (containment for the spillage around the tanks only)
Volume is proposed to be contained within the surrounding area. Where currently permeable (grassed area), to be made impermeable - concrete surface. Volume is proposed to be contained within the road around the tanks. Hardstanding area around tank to cascade sludge down to road level. Speed humps to ensure volume is contained within the area.
Freeboard allowance
Due to small flow from loss of containment, wave action, which could potentially overtop the bund, not accounted for. No freeboard allowance thus included,
Type of drainage to be provided
Volume is proposed to be contained within bund with no connection to downstream drainage. All existing drainage to be removed. Mobile pumps to be used to remove volume from bund from low point. Daily operational inspection to ensure any rainfall runoff within the bund is removed.
14/08/2020
File Ref
Version
B14411-123532-ZZ-XX-AS-ZA-CI1007
P01
Originator
Jacques Calitz
James Croston
Date
Date
30/06/2020
14/08/2020
Checker
Zone 6 (Digested sludge holding tanks)
IED CIRIA 736 Risk Assessment
James Croston
Approver
Date

## List (hidden)
Possible Combination |  |  |  | Site Hazard Rating | LLL | MLL | HLL
L | L | L | LLL | L | LLM | MLM | HLM
M | M | L | MML | L | LLH | MLH | HLH
M | L | L | MLL | L | LMM | MMM | HMM
H | L | L | HLL | L | LML | MML | HML
M | M | M | MMM | M | LMH | MMH | HMH
H | M | L | HML | M | LHL | MHL | HHL
H | H | L | HHL | M | LHM | MHM | HHM
H | M | M | HMM | H | LHH | MHH | HHH
H | H | M | HHM | H
H | H | H | HHH | H
> 1 in 100 |  |  | H
1 in 100 to 1 in 1 Million |  |  | M
< 1 in 1 Million |  |  | L
H | H | HH | High
H | M | HM | High
M | H | MH | High
M | M | MM | Moderate
H | L | HL | Moderate
L | H | LH | Moderate
L | L | LL | Low
M | L | ML | Low
L | M | LM | Low
Low |  | Class 1
Moderate |  | Class 2
High |  | Class 3