## Current asset evaluation
Zone 8 - Cake bays
Description | Cake is transferred to the three cake bays from the centrifuge building.
Number of tanks | 3
Volume of tank | Not applicable - sludge is stored within area but not contained within
Material of tank | Concrete - storage area is made from pre-cast concrete retaining wall units and base is concrete
Above/below ground? | Above ground - bays
Pipe material | Not known - no details on drawings
Drainage for zone | Road around centrifuge and cake bays drains through gullies which return back to the liquors return tank.
Year of construction | 2002
Surrounding area | Cake bays area has a concrete base. Surrounding external area is grass, block paving and tarmac.
Is asset fit for purpose? | The cake bays were originally designed and constructed to hold cake and has been operating with no notable concerns. Cake bays has not undergone a change of use
Condition of the tank Any tank failures - cracks, flaking, corrosion, overflows, overfilling? | No issues noted from operations
Condition of pipework Pipe leaks, corrosion? | Gullies don’t work - full of cake - run-off cascades down road towards PSTs
Protection of assets - bollards? | No vehicle impact protection - no known damage
Control/monitoring/alarming measures in place? | Operator controlled
Secondary containment provided? | None
Secondary containment condition? | N/A
14/08/2020
File Ref
Version
B14411-123532-ZZ-XX-AS-ZA-CI1009
P01
Originator
Jacques Calitz
James Croston
Date
Date
30/06/2020
14/08/2020
Checker
Zone 8 (Cake bays)
IED CIRIA 736 Risk Assessment
James Croston
Approver
Date

## Risk assessment
Source
Material | Physical properties | Maximum quantity | units | Storage | Flammability | Corrosive | Ecotoxicity (based on LD and quantity) | Hazard rating
Cake bays - 3 in total | Cake formed from indigenous and imported sludge | Not applicable - sludge is stored within area but not contained within | m3 | Concrete bay - open top (above ground) | Not flammable | Possibly | Organic heavy - Nitrogen, Phosphorous, Ammonia, BOD, TSS, COD - Environmental hazard (algae blooms and death of organisms) Pathogens - Human hazard (E.coli etc.) | M
Rainwater run-off contaminated by inventory | Surface water mixed with sludge/pollutants | Dependent on area of containment | m3 | N/A | Not flammable | No | Lower concentration of sludge contaminants | L
[7 empty] | Overall | M
Pathway and Receptor
Pathway - the route from primary containment to receptor (extent of loss of containment) |  | Time of concentration/ duration of source outside containment |  | Hazard - Transport potential |  |  | Receptor | Hazard - Damage potential
Tanks are surrounded by permeable grass. Based on available ground information, soil is permeable (infiltration rate of 4 x 10-5m/s) Permeable sub-soils/strata will thus act as a pathway |  | Direct contamination but over an extended period of time |  | M |  |  | Groundwater (underlain by a secondary aquifer) - contaminated through percolation through soil or through fluctuating tidal groundwater level Over a very long period, can contaminate river Dee through groundwater base flow underground | M
Tidally fluctuating groundwater |  | Direct contamination but over an extended period of time |  | M
Existing underground services - ductwork, tunnels etc. (locations not known) |  | Direct contamination but over an extended period of time |  | L
Existing underground sludge pipework |  | Direct contamination but over an extended period of time |  | M
Impermeable ground - overland flow (if ground is saturated/blocked or contents spill onto the road) Overland flow gets discharged into gullies connected to liquor return tank. Potential that some of the gullies discharge directly to ditch downstream closer to PSTs. |  | Minutes - hours |  | H |  |  | WWTW - liquor return tank pumps liquor back to head of works | M
*Flood water - Site is within flood zone 3 (operational staff did however mention no flooding has been recorded within the site) |  | Minutes - N/A (dependant on flooding extent) |  | L |  |  | River Dee - animals and fish (290m away) | H
|  | Overall |  | M |  |  | Overall | M
*Flooding in flood zone 3 only have a 1 in 100 year probability of happening in a year
Combination of Hazards | MMM
Overall risk rating for zone (Ciria 736) | M
Frequency of loss of containment
Failure mode | Description | Existing consequence and mitigation measure | [6 empty] | Annual probability of loss of containment | Rating
Large storm event - high run-off and contaminated run-off (partial) | Blocked gullies and contaminated surface water is transferred downstream | There are existing gullies at each of the cake bays to drain away any liquid. Based on discussions with operational staff, the gullies are generally full of cake and not operating as they should. Contaminated run-off gets cascaded down the road towards the PSTs and drain into the road drainage downstream. | [6 empty] | 1 in 100 to 1 in 1 Million | M
Flooding (partial) | River flooding - Flood zone 3 - potential contamination with cake | No flooding has been reported/recorded by the operators There could be a potential for the flood water to be contaminated due to cake. | [6 empty] | < 1 in 1 Million | L
*Site is manned. Probability and frequency thus reduced
Frequency of loss of containment (Ciria 736) | M
Overall zone hazard rating
Overall zone hazard rating (Ciria 736) | Moderate
Containment required
Containment required | Class 2
Overland flow paths
Impermeable ground
Permeable ground
Road gullies
250m
230m
290m
River Dee
Liquor return at head of works
3rd party land
Ditch
93m
14/08/2020
File Ref
Version
B14411-123532-ZZ-XX-AS-ZA-CI1009
P01
Originator
Jacques Calitz
James Croston
Date
Date
30/06/2020
14/08/2020
Checker
Zone 8 (Cake bays)
IED CIRIA 736 Risk Assessment
James Croston
Approver
Date
Note on J16: Calitz, Jacques: Add manually. Based on highest risk rating
Note on F60: Calitz, Jacques: Add manually. Based on highest risk rating
Note on J60: Calitz, Jacques: Add manually. Based on highest risk rating
Note on C83: Calitz, Jacques: Add manually. Based on highest risk rating

## Mitigation
Catastrophic failure - modes (loss of containment) - pragmatic solution
Risk | Cause | Existing consequence and mitigation measure | Existing zone risk rating | Proposed Mitigation | Risk rating after mitigation
| Blocked gullies and contaminated surface water is transferred downstream | There are existing gullies at each of the cake bays to drain away any liquid. Based on discussions with operational staff, the gullies are generally full of cake and not operating as they should. Contaminated run-off gets cascaded down the road towards the PSTs and drain into the road drainage downstream. | L | The existing cake bays do not act as containment features rather like temporary storage. General failure mechanisms not applicable. There is however cases where contaminated rainfall run-off is cascaded downstream when the gullies are blocked (most cases). There is thus the potential to contaminate potential permeable areas downstream. Critical failure is thus the contaminated run-off generated from the impermeable area around the cake bays cascading downstream. | L
| Flooding (partial) | No flooding has been reported/recorded by the operators There could be a potential for the flood water to be contaminated due to cake. | L | No mitigation measures proposed. | L
The probability and risk of failure from the tanks is low and any associated loss of inventory volume would be contained within the adjacent hardstanding area. In line with CIRIA 736, the existing mitigation measures are adequate provided the drainage within the zone is refurbished/replaced. The site maintenance strategy and annual plant shutdown does need to include structural assessments of the containment structures, including the surrounding hardstanding areas. Drainage pipework and above ground process pipework should be inspected by a competent engineer to allow for pro-active maintenance.
14/08/2020
File Ref
Version
B14411-123532-ZZ-XX-AS-ZA-CI1009
P01
Originator
Jacques Calitz
James Croston
Date
Date
30/06/2020
14/08/2020
Checker
Zone 8 (Cake bays)
IED CIRIA 736 Risk Assessment
James Croston
Approver
Date

## Containment req. volume (full)
Secondary containment volume requirement - Rainfall volume
Area of containment | 380 | m2 | (Area of containment)
24 hour - 1:10 year rainfall | 41 | mm
8 day - 1:10 year rainfall |  | mm
Total rainfall volume | 15.58 | m3
Total secondary containment volume
Volume | 15.58 | m3
14/08/2020
File Ref
Version
B14411-123532-ZZ-XX-AS-ZA-CI1009
P01
Originator
Jacques Calitz
James Croston
Date
Date
30/06/2020
14/08/2020
Checker
Zone 8 (Cake bays)
IED CIRIA 736 Risk Assessment
James Croston
Approver
Date

## Pragmatic - volume and type
Catastrophic failure - modes (total loss of containment) - pragmatic solution
Failure mode | Solution
Overland flow downstream - blocked gullies | To avoid blockage of gullies, to allow for daily cleaning (less desirable) Construct new gullies and a threshold drain closer to road entrance. Current gully location is right under cake and probability of blockage is very high. Locating them further downstream reduces blockage and removes risk of run-off cascading downstream.
Implementing the above measures will significantly reduce the probability and risk of failure from the cake bays and negate the need for secondary containment. As per CIRIA 736, the above will need to be implemented in conjunction with a good maintenance strategy
Proposed gullies
Existing gullies
Proposed threshold drain
14/08/2020
File Ref
Version
B14411-123532-ZZ-XX-AS-ZA-CI1009
P01
Originator
Jacques Calitz
James Croston
Date
Date
30/06/2020
14/08/2020
Checker
Zone 8 (Cake bays)
IED CIRIA 736 Risk Assessment
James Croston
Approver
Date

## Containment type
Containment to be provided
Based on a Moderate site risk rating for the zone, Class 2 containment is required.
Catastrophic failure
Catastrophic failure assumes the contaminated run-off generated from the impermeable area around the cake bays is cascaded downstream
Material type of containment to be provided
Type |  |  | Applicability
Reinforced concrete/masonry flooring and bund |  |  | Due to small volume from loss of containment, use of a masonry/concrete bund is appropriate. Existing kerb (125mm) can be used.
Earth banked basins, bunds and flooring |  |  | Soil within site is of permeable nature - Clay or impermeable soil type not plentiful Potential for stabilised soil (lime and cement used to make it impermeable) Area of which bunding can be provided is however limited - assuming a bund height of 300mm, crest width of 100m, side slopes of 1:3 - a base width of the bund of at least 2000mm is required Dependant on area required and nature of surrounding area, might be applicable. Surrounding area is full of pipework and structures providing limited space for an earth bund.
Containment tank |  |  | Nature of catastrophic failure and type of containment makes use of a containment tank not appropriate
Type of containment to be provided
Options considered:
Option 1: Local containment (containment around the bays only)
Volume is proposed to be contained within the surrounding area. Area is currently impermeable. Volume is proposed to be contained in hardstanding around the tanks and within the road around the tanks. Current kerb to be used along hardstanding area if possible. Localised speed bump to be utilised at entrance to cake bays to allow for bund area.
Area required (estimated) - local containment
Volume 100% | Height of containment | Area based on flat ground
15.58 | 100 | 155.8
15.58 | 125 | 124.64
Freeboard allowance
Due to small flow from loss of containment, wave action, which could potentially overtop the bund, not accounted for. No freeboard allowance thus included,
Type of drainage to be provided
Volume is proposed to be contained within bund with no connection to downstream drainage. All existing drainage to be removed. Mobile pumps to be used to remove volume from bund from low point. Daily operational inspection to ensure any rainfall runoff within the bund is removed.
Freeboard allowance
380m2 area for run-off
Existing 125mm kerb
Potential 100/125mm speed hump to close zone off
14/08/2020
File Ref
Version
B14411-123532-ZZ-XX-AS-ZA-CI1009
P01
Originator
Jacques Calitz
James Croston
Date
Date
30/06/2020
14/08/2020
Checker
Zone 8 (Cake bays)
IED CIRIA 736 Risk Assessment
James Croston
Approver
Date

## List (hidden)
Possible Combination |  |  |  | Site Hazard Rating | LLL | MLL | HLL
L | L | L | LLL | L | LLM | MLM | HLM
M | M | L | MML | L | LLH | MLH | HLH
M | L | L | MLL | L | LMM | MMM | HMM
H | L | L | HLL | L | LML | MML | HML
M | M | M | MMM | M | LMH | MMH | HMH
H | M | L | HML | M | LHL | MHL | HHL
H | H | L | HHL | M | LHM | MHM | HHM
H | M | M | HMM | H | LHH | MHH | HHH
H | H | M | HHM | H
H | H | H | HHH | H
> 1 in 100 |  |  | H
1 in 100 to 1 in 1 Million |  |  | M
< 1 in 1 Million |  |  | L
H | H | HH | High
H | M | HM | High
M | H | MH | High
M | M | MM | Moderate
H | L | HL | Moderate
L | H | LH | Moderate
L | L | LL | Low
M | L | ML | Low
L | M | LM | Low
Low |  | Class 1
Moderate |  | Class 2
High |  | Class 3