## List of forms concise
Form | Title
IED HR1 | ANNUAL OPERATING HOURS RETURN |  | Annual
Annual operating hours return. For each LCP: Annual operating hours. For each LCP with a Limited Lifetime Derogation or a 10,000h monitoring derogation: cumulative operating hours from 1 Jan 2016. For each LCP or Unit with a 1,500h derogation: annual derogated operating hours (from entry date in first year) and 5 year running average from entry date. For a combined cycle gas turbine that operates with a bypass stack in normal operation, the bypass hours during normal operation are inlcuded in the plant hours but are also reported separately.
IED RTA1 | QUARTERLY RETURN OF MONTHLY SO2, NOx AND DUST MASS RELEASE DATA |  | QTRLY
Quarterly mass emissions return for plant in the TNP or with a Site Specific NOx limit. TNP and IED inventory (for every LCP): Mass emissions excluding start-up and shut-down. Site Specific NOx limits (additional report if applicable): Mass emissions including start-up and shut-down.
IED AR1 | ANNUAL RETURN OF ENERGY INPUT AND TOTAL EMISSIONS
IED Inventory annual energy and annual mass emissions return.
IED CON 1 / IED CON 2 | QUARTERLY RETURN OF MONTHLY MEAN, MONTHLY MAXIMUM DAILY MEAN AND ANNUAL RETURN OF HOURLY CONCENTRATION PERCENTILES |  | QTRLY
Quarterly return for each LCP (and each Unit with a 1,500h derogation regarded as a separate LCP). Validated concentration data: Monthly mean; Maximum daily mean within month (applied as 95th percentile in the interim BAT period for some plant); Annual 95th percentile of hourly averages.
IED PM1 | SIX-MONTHLY RETURN OF DISCONTINUOUS MONITORING RESULTS (AS REQUIRED)
IED BD1
IED MF1 | RETURN OF MALFUNCTION AND BREAKDOWN DATA (AS REQUIRED) | Not Req
Validated concentration data for each day affected by Malfunction or Breakdown.
IED CEM 1 | CONTINUOUS MEASUREMENT SYSTEMS INVALIDATION LOG |  | Annual
Quarterly CEMs Invalidation Log for each LCP as required by the IED Chapter III Monitoring Requirements
REM 1 | RESOURCE EFFICIENCY METRICS | Not Req
Annual Installation Resource Efficiency Metrics for Electricity Supply Industry Sub-Sector

## (Form 1)(QTR) - IED RTA1
FORM NAME
V.10.6 Oct 2015
Releases of IED Pollutants to Air
| Operational Summary for the year |  | 2021
| Operator: Dragon LNG | A
#VALUE!
| Site Location: | Dragon LNG, Milford Haven
| Original permit number: | EPR/AP3136UA/V004
Note: beginning 1 January 2016, a return is required for each LCP within 28 days of the end of each quarter
| Emissions | SO2 | NOx | Dust
|  | (tonnes) | (tonnes) | (tonnes) |  | Dragon Cogen LCP no longer exists.
| January | 0 | 0 | 0
| February | 0 | 0 | 0
| March | 0 | 0 | 0
| Total for Quarter 1 | 0 | 0 | 0
| April | 0 | 0 | 0
| May | 0 | 0 | 0
| June | 0 | 0 | 0
| Total for Quarter 2 | 0 | 0 | 0
| July | 0 | 0 | 0
| August | 0 | 0 | 0
| September | 0 | 0 | 0
| Total for Quarter 3 | 0 | 0 | 0
October
November
December
| Total for Quarter 4 | 0 | 0 | 0
| Annual Total | 0 | 0 | 0
I confirm that this data is not knowingly reported with any omissions, errors or misrepresentation. All measurement equipment used to generate the data has been appropriately calibrated and maintained regularly; this includes calibration against traceable international measurement standards where available. The data is supported by appropriate record keeping. IT is designed, documented, tested, implemented, controlled and maintained to ensure reliable, accurate and timely processing of data; data handling and calculations have been appropriate; data has been checked for false and unusual measurements. The annual report of emissions for the above participating large combustion plant has been verified in accordance with the requirements of the Transitional National Plan Regulations.
| Name of the operator staff responsible for the quality of data supplied to the Register in accordance with the principles above. | P Wilson |  | Date | 2022-04-26
NOTES:
1. Data must be reported in tonnes to 2 decimal places.
2. All forms must be saved in the format IED RTA1—Quarter-Inventory Year-DEFRA IED LCP Number i.e. IED RTA1-Q1-2015-XXX for upload purposes
3. No PDF documents shall be accepted
4. Upload Forms held on GOV.UK will be accepted other variants of the forms will be automatically rejected which may impact their statutory obligations to report on time

## (Form-2)(QTR)-IED CON1(A1-COGN)
RELEASES TO AIR
QUARTERLY RETURN
MONTHLY MEAN, MAXIMUM DAILY MEAN AND ANNUAL PERCENTILE CONCENTRATIONS (a),(b),(c)
Operator: Dragon LNG |  |  |  |  | Form: |  | IED CON1 (COGEN-Main Stack)
Location: Waterston, Milford Haven |  |  |  |  | Version/date: |  | V.2.1 31 Dec 2015
Permit/Variation Number: EPR/AP3136UA/V004.
Year: LCP: | SO2 (mg/m3) |  | NOx (mg/m3) |  | Dust (mg/m3) |  | Monthly
Month | Monthly Mean | Max Daily Mean | Monthly Mean | Max Daily Mean | Monthly Mean | Max Daily Mean (f) | Fuel S % | FGD Eff (d) %
January | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Dragon Cogen LCP no longer exists.
February | 0 | 0 | 0 | 0 | 0 | 0
March | 0 | 0 | 0 | 0 | 0 | 0
April | 0 | 0 | 0 | 0 | 0 | 0
May | 0 | 0 | 0 | 0 | 0 | 0
June | 0 | 0 | 0 | 0 | 0 | 0
July | 0 | 0 | 0 | 0 | 0 | 0
August | 0 | 0 | 0 | 0 | 0 | 0
September | 0 | 0 | 0 | 0 | 0 | 0
October
November
December
Monthly ELV/Daily ELV (e)
Annual 95th Percentile (f)
Annual Percentile ELV (g)
NOTES:
(a) All concentration data are based on validated hourly average concentrations excluding start-up and shut-down and periods of malfunction or breakdown of abatement equipment
(b) Annual percentiles of hourly average concentrations are submitted with the final return (Quarter 4)
(c) Reference conditions. Solid fuel: 6% O2 (dry) Liquid fuel: 3% O2 (dry) at 273.15K, 101.325 kPa
(d) Required for indigenous fuel derogation only - state target removal efficiency as the ELV (if applicable)
(e) Leave the Daily ELV blank if this is applied as a 95th percentile ELV within the Permit
(f) For each pollutant, report the Annual 95th percentile of hourly averages in the first column and, if applicable, Annual 95th percentile of daily means in the second column
(g) For each pollutant, report Annual 95th percentile ELV for hourly averages in the first column and, if applicable, Annual 95th percentile ELV for daily means in the second column
Signed on behalf of the Operator by: |  | P Wilson
Date of return: |  | 2022-04-26

## (Form-3)(QTR)-IED CON2(A-COGN)
RELEASES TO AIR
QUARTERLY RETURN
MONTHLY MEAN, MAXIMUM DAILY MEAN AND ANNUAL PERCENTILE CONCENTRATIONS (a),(b),(c)
OPERATING MODE:
Operator: Dragon LNG |  |  | Form: |  | IED CON 2 (COGEN Main Stack)
Location: Waterston, Milford Haven |  |  | Version/date: |  | V.2.1 31 Dec 2015
Permit/Variation Number: EPR/AP3136UA/V004.
Year: | LCP:
| NOx (mg/m3) |  |  | CO (mg/m3)
Month | Monthly Mean (d) | Max Daily Mean (d) | Part Load Max Daily Mean (e) | Monthly Mean (d) | Max Daily Mean (d) | Part Load Max Daily Mean (e)
January | 0 | 0 | 0 | 0 | 0 | 0 | Dragon Cogen LCP no longer exists.
February | 0 | 0 | 0 | 0 | 0 | 0
March | 0 | 0 | 0 | 0 | 0 | 0
April | 0 | 0 | 0 | 0 | 0 | 0
May | 0 | 0 | 0 | 0 | 0 | 0
June | 0 | 0 | 0 | 0 | 0 | 0
July | 0 | 0 | 0 | 0 | 0 | 0
August | 0 | 0 | 0 | 0 | 0 | 0
September | 0 | 0 | 0 | 0 | 0 | 0
October
November
December
Monthly ELV/Daily ELV (f) | 75 | 82.5 |  | 100 | 110
Annual 95th Percentile (g)
Annual Percentile ELV (h) | 150 |  |  | 200
NOTES:
(a) All data based on validated hourly average concentrations, excluding start-up and shut-down and periods of malfunction or breakdown of abatement equipment, at 15% O2, dry, 273.15K, 101.325 kPa
(b) Annual percentiles are submitted with the final return (Quarter 4)
(c) Extend report to cover the required number of LCP on each site and repeat report for each separately regulated Operating Mode as required, e.g., Combined Cycle, Open Cycle, Supplementary firing, Auxiliary firing
(d) Averages determined at loads in the range 70% < Load ≤ 100% ISO base load and above
(e) Averages determined at loads in the range MSUL* < Load ≤ 100% ISO base load and above (* For a 3 parameter approach, from the point of Start-Up to the point of Shut-down)
(f) Leave the Daily ELV blank if this is applied as a 95th percentile ELV within the Permit
(g) For each pollutant, report the Annual 95th percentile ELV for hourly averages in the first column and, if applicable, the Annual 95th percentile ELV for daily means in the second column
(h For each pollutant, report the Annual 95th percentile of hourly averages in the first column and, if applicable, the Annual 95th percentile of daily means in the second column
Signed on behalf of the Operator by: |  |  | P Wilson
Date of return: |  |  | 26.10.21

## (Form-4)(QTR)-IED CON2(A8-SCV1)
RELEASES TO AIR
QUARTERLY RETURN
MONTHLY MEAN, MAXIMUM DAILY MEAN AND ANNUAL PERCENTILE CONCENTRATIONS (a),(b),(c)
OPERATING MODE:
Operator: Dragon LNG |  |  | Form: |  | IED CON 2 (Submerged Combustion Vapouriser(SCV))
Location: Waterston, Milford Haven |  |  | Version/date: |  | V.2.1 31 Dec 2015
Permit/Variation Number: EPR/AP3136UA/V004.
Year: 2022 | Submerged Combustion Vapouriser(SCV)
| NOx (mg/m3) |  |  | CO (mg/m3)
Month | Monthly Mean (d) | Max Daily Mean (d) | Part Load Max Daily Mean (e) | Monthly Mean (d) | Max Daily Mean (d) | Part Load Max Daily Mean (e)
January | 14.2955 |  |  | 21.512
February | 9.6332 |  |  | 19.449
March | 8.7003 |  |  | 14.836
April
May
June
July
August
September
October
November
December
Monthly ELV/Daily ELV (f)
Annual 95th Percentile (g)
Annual Percentile ELV (h)
NOTES:
(a) All data based on validated hourly average concentrations, excluding start-up and shut-down and periods of malfunction or breakdown of abatement equipment, at 15% O2, dry, 273.15K, 101.325 kPa
(b) Annual percentiles are submitted with the final return (Quarter 4)
(c) Extend report to cover the required number of LCP on each site and repeat report for each separately regulated Operating Mode as required, e.g., Combined Cycle, Open Cycle, Supplementary firing, Auxiliary firing
(d) Averages determined at loads in the range 70% < Load ≤ 100% ISO base load and above
(e) Averages determined at loads in the range MSUL* < Load ≤ 100% ISO base load and above (* For a 3 parameter approach, from the point of Start-Up to the point of Shut-down)
(f) Leave the Daily ELV blank if this is applied as a 95th percentile ELV within the Permit
(g) For each pollutant, report the Annual 95th percentile ELV for hourly averages in the first column and, if applicable, the Annual 95th percentile ELV for daily means in the second column
(h For each pollutant, report the Annual 95th percentile of hourly averages in the first column and, if applicable, the Annual 95th percentile of daily means in the second column
Signed on behalf of the Operator by: |  |  | P Wilson
Date of return: |  |  | 2022-04-26

## (Form-6) - IED PM1-SCV1
RELEASES TO AIR
RETURN OF DISCONTINUOUS MONITORING RESULTS
Location: Waterston, Milford Haven |  | Form: |  | IED PM1
Permit/Variation Number: EPR/AP3136UA/V004. |  | Version: |  | V.2.1 31 Dec 2015
Year: 2022 | SCV1 combustion(Emission Point A8)
Six months to -
Measurement approach | NOx | SO2 | CO | Hg | Dust
Time: 11:55 to 12:55
Date: 09/03/2022
Measurement 1 (mg/m3)(b) | 57.8 |  | 15.8
Measurement 2 (mg/m3)(b)
Measurement 3 (mg/m3)(b)
Alternative approach(c)
Method(d)
Calculation (mg/m3)
Operational data(a)
Load (%MCR) | 100%
Fuel 1 name (%) | Natural Gas (100%)
Fuel 2 name (%) | N/A |  | N/A
Fuel 3 name (%) | N/A |  | N/A
Daily Emission Limit Value
(mg/m3) | 86 |  | 130
NOTES:
(a) Operational data for the test period (measurement approach) or the six month period to date (Alternative approach)
(b) Reference conditions for mg/m3 are 15% O2 CCGT, 6% O2 solid fuels, 3% O2 for oil and gas, dry, 0°C, 101.325 kPa
(c) Alternative approach to discontinuous monitoring by agreement with the Competent Authority
(d) Use abbreviation: NF for agreed NOx factor, FS for fuel sulphur content, CS for agreed CO factor, DF for agreed dust factor
Signed on behalf of the Operator by: |  | P Wilson
Date of return: |  | 2022-04-26

## (Form-6) - IED PM1-SCV2
RELEASES TO AIR
RETURN OF DISCONTINUOUS MONITORING RESULTS
Location: Waterston, Milford Haven |  | Form: |  | IED PM1
Permit/Variation Number: EPR/AP3136UA/V004. |  | Version: |  | V.2.1 31 Dec 2015
Year: 2022 | SCV2 combustion(Emission Point A9)
Six months to -
Measurement approach | NOx | SO2 | CO | Hg | Dust
Time : 13:21 to 14:21
Date: 09/03/2022
Measurement 1 (mg/m3)(b) | 67.8 |  | 15.5
Measurement 2 (mg/m3)(b)
Measurement 3 (mg/m3)(b)
Alternative approach(c)
Method(d)
Calculation (mg/m3)
Operational data(a)
Load (%MCR) | 100%
Fuel 1 name (%) | Natural Gas (100%)
Fuel 2 name (%) | N/A |  | N/A
Fuel 3 name (%) | N/A |  | N/A
Daily Emission Limit Value
(mg/m3) | 86 |  | 130
NOTES:
(a) Operational data for the test period (measurement approach) or the six month period to date (Alternative approach)
(b) Reference conditions for mg/m3 are 15% O2 CCGT, 6% O2 solid fuels, 3% O2 for oil and gas, dry, 0°C, 101.325 kPa
(c) Alternative approach to discontinuous monitoring by agreement with the Competent Authority
(d) Use abbreviation: NF for agreed NOx factor, FS for fuel sulphur content, CS for agreed CO factor, DF for agreed dust factor
Signed on behalf of the Operator by: |  | P Wilson
Date of return: |  | 2022-04-26

## (Form-6) - IED PM1-SCV3
RELEASES TO AIR
RETURN OF DISCONTINUOUS MONITORING RESULTS
Location: Waterston, Milford Haven |  | Form: |  | IED PM1
Permit/Variation Number: EPR/AP3136UA/V004. |  | Version: |  | V.2.1 31 Dec 2015
Year: | SCV3 combustion(Emission Point A10)
Six months to -
Measurement approach | NOx | SO2 | CO | Hg | Dust
Time : 14:54 to 15:54
Date: 09/03/2022
Measurement 1 (mg/m3)(b) | 70.8 |  | 15.7
Measurement 2 (mg/m3)(b)
Measurement 3 (mg/m3)(b)
Alternative approach(c)
Method(d)
Calculation (mg/m3)
Operational data(a)
Load (%MCR) | 100%
Fuel 1 name (%) | Natural Gas (100%)
Fuel 2 name (%) | N/A |  | N/A
Fuel 3 name (%) | N/A |  | N/A
Daily Emission Limit Value
(mg/m3) | 86 |  | 130
NOTES:
(a) Operational data for the test period (measurement approach) or the six month period to date (Alternative approach)
(b) Reference conditions for mg/m3 are 15% O2 CCGT, 6% O2 solid fuels, 3% O2 for oil and gas, dry, 0°C, 101.325 kPa
(c) Alternative approach to discontinuous monitoring by agreement with the Competent Authority
(d) Use abbreviation: NF for agreed NOx factor, FS for fuel sulphur content, CS for agreed CO factor, DF for agreed dust factor
Signed on behalf of the Operator by: |  | P Wilson
Date of return: |  | 2022-04-26

## (Form-6) - IED PM1-SCV4
RELEASES TO AIR
RETURN OF DISCONTINUOUS MONITORING RESULTS
Location: Waterston, Milford Haven |  | Form: |  | IED PM1
Permit/Variation Number: EPR/AP3136UA/V004. |  | Version: |  | V.2.1 31 Dec 2015
Year: 2022 | SCV4 combustion(Emission Point A11)
Six months to -
Measurement approach | NOx | SO2 | CO | Hg | Dust
Time : 16:17 to 17:17
Date: 09/03/2022
Measurement 1 (mg/m3)(b) | 57.7 |  | 20.2
Measurement 2 (mg/m3)(b)
Measurement 3 (mg/m3)(b)
Alternative approach(c)
Method(d)
Calculation (mg/m3)
Operational data(a)
Load (%MCR) | 100%
Fuel 1 name (%) | Natural Gas (100%)
Fuel 2 name (%) | N/A |  | N/A
Fuel 3 name (%) | N/A |  | N/A
Daily Emission Limit Value
(mg/m3) | 86 |  | 130
NOTES:
(a) Operational data for the test period (measurement approach) or the six month period to date (Alternative approach)
(b) Reference conditions for mg/m3 are 15% O2 CCGT, 6% O2 solid fuels, 3% O2 for oil and gas, dry, 0°C, 101.325 kPa
(c) Alternative approach to discontinuous monitoring by agreement with the Competent Authority
(d) Use abbreviation: NF for agreed NOx factor, FS for fuel sulphur content, CS for agreed CO factor, DF for agreed dust factor
Signed on behalf of the Operator by: |  | P Wilson
Date of return: |  | 2022-04-26

## (Form-6) - IED PM1-SCV5
RELEASES TO AIR
RETURN OF DISCONTINUOUS MONITORING RESULTS
Location: Waterston, Milford Haven |  | Form: |  | IED PM1
Permit/Variation Number: EPR/AP3136UA/V004. |  | Version: |  | V.2.1 31 Dec 2015
Year: 2022 | SCV5 combustion(Emission Point A12)
Six months to -
Measurement approach | NOx | SO2 | CO | Hg | Dust
Time : 09:45 to 10:45
Date: 10/03/2022
Measurement 1 (mg/m3)(b) | 60 |  | 7.2
Measurement 2 (mg/m3)(b)
Measurement 3 (mg/m3)(b)
Alternative approach(c)
Method(d)
Calculation (mg/m3)
Operational data(a)
Load (%MCR) | 100%
Fuel 1 name (%) | Natural Gas (100%)
Fuel 2 name (%) | N/A |  | N/A
Fuel 3 name (%) | N/A |  | N/A
Daily Emission Limit Value
(mg/m3) | 86 |  | 130
NOTES:
(a) Operational data for the test period (measurement approach) or the six month period to date (Alternative approach)
(b) Reference conditions for mg/m3 are 15% O2 CCGT, 6% O2 solid fuels, 3% O2 for oil and gas, dry, 0°C, 101.325 kPa
(c) Alternative approach to discontinuous monitoring by agreement with the Competent Authority
(d) Use abbreviation: NF for agreed NOx factor, FS for fuel sulphur content, CS for agreed CO factor, DF for agreed dust factor
Signed on behalf of the Operator by: |  | P Wilson
Date of return: |  | 2022-04-26

## (Form-6) - IED PM1-SCV6
RELEASES TO AIR
RETURN OF DISCONTINUOUS MONITORING RESULTS
Location: Waterston, Milford Haven |  | Form: |  | IED PM1
Permit/Variation Number: EPR/AP3136UA/V004. |  | Version: |  | V.2.1 31 Dec 2015
Year: 2022 | SCV6 combustion(Emission Point A13)
Six months to -
Measurement approach | NOx | SO2 | CO | Hg | Dust
Time : 12:13 to 13:13
Date: 10/03/2022
Measurement 1 (mg/m3)(b) | 69.7 |  | 7.1
Measurement 2 (mg/m3)(b)
Measurement 3 (mg/m3)(b)
Alternative approach(c)
Method(d)
Calculation (mg/m3)
Operational data(a)
Load (%MCR) | 100%
Fuel 1 name (%) | Natural Gas (100%)
Fuel 2 name (%) | N/A |  | N/A
Fuel 3 name (%) | N/A |  | N/A
Daily Emission Limit Value
(mg/m3) | 86 |  | 130
NOTES:
(a) Operational data for the test period (measurement approach) or the six month period to date (Alternative approach)
(b) Reference conditions for mg/m3 are 15% O2 CCGT, 6% O2 solid fuels, 3% O2 for oil and gas, dry, 0°C, 101.325 kPa
(c) Alternative approach to discontinuous monitoring by agreement with the Competent Authority
(d) Use abbreviation: NF for agreed NOx factor, FS for fuel sulphur content, CS for agreed CO factor, DF for agreed dust factor
Signed on behalf of the Operator by: |  | P Wilson
Date of return: |  | 2022-04-26

## (Form-4) - IED HR1
RELEASES TO AIR
ANNUAL RETURN
OPERATING HOURS
Operator: Dragon LNG |  |  |  |  | Form: |  | IED HR1
Location: Waterston, Milford Haven |  |  |  |  | Version/date: |  | V.2.1 31 Dec 2015
Permit/Variation Number: EPR/AP3136UA/V004.
Year: | LCP1 (hours) | Bypass (hours) | LCP2 (hours) | Bypass (hours) | LCP3 (hours) | Bypass (hours) | LCP4 (hours) | Bypass (hours)
Annual Operating Hours (a), (b)
Cumulative Operating Hours (c),(d)
Derogated annual hours (e)
Five year rolling average (f)
NOTES:
(a) Annual operating hours for every LCP from 1-Jan in calendar year. (For gas turbines with a Bypass stack, include the Bypass stack operating hours during normal operation even though these are reported separately).
(b) For gas turbines with a Bypass stack, report Bypass operating hours from 1-Jan in calendar year, excluding Start-Up and Shut-down, in the adjacent column (labelled Bypass) which may be deleted if not applicable.
(c) Cumulative operating hours from 1-Jan-2016 for LCP subject to a Limited Lifetime Derogation or a 10,000h monitoring derogation. (For gas turbines with a Bypass stack, include the Bypass stack operating hours during normal operation even though these are reported separately).
(d) For gas turbines with a Bypass stack, report Bypass Cumulative operating hours from 1-Jan-2016 if subject to a separate 10,000h monitoring derogation, in the adjacent column (labelled Bypass).
(e) Annual operating hours in calendar year from entry date (in first year as applicable) or from 1-Jan in calendar year, for each 1,500h ELV derogated Unit/LCP only.
(f) Five year running average from entry date for each 1,500h derogated Unit/LCP only.
(g) General note: hours are reported as a decimal number to two decimal places.
Signed on behalf of the Operator by:
Date of return:

## (Form 5) - IED AR1
Form Name
V.10.6 Oct 2015
IED Reporting - Energy Usage & Emissions for the year: | 2021
Operator: | Dragon LNG
#N/A
Site Location: | Waterston, Milford Haven
Permit/Variation number: | EPR/AP3136UA/V004.
LCP Net Rated Thermal Input Capacity (MW):
By Fuel
Parameter | TOTAL | Coal | Lignite | Peat | Biomass | Other solid fuels | Liquid fuels | Natural gas | Other gases
Annual energy input (TJ)
Total Annual SO2 emission (tonnes)
Total Annual NOx emission (tonnes)
Total Annual Dust (PM) emission (tonnes)
Signed on behalf of the Operator |  |  | Date
NOTES:
(a) Annual energy input must be reported in TJ to 1 decimal places
(b) Annual emissions to air must be reported to 2 decimal places and exclude start-up and shut-down
(c) All forms must be saved in the format IED AR1—DEFRA IED LCP Number - Inventory Year i.e. IED AR1-XXX-2013
(d) No PDF documents shall be accepted
(e) Upload Forms held on GOV.UK will be accepted other variants of the forms will be automatically rejected which may impact their statutory obligations to report on time

## (Form-7) - IED CEM1
CONTINUOUS MEASUREMENT SYSTEMS INVALIDATION LOG
QUARTERLY RETURN
Operator: |  |  |  | Form: | IED CEM1
Monitor positioned on release point/LCP Number: |  | / |  | Version/date: | V.2.1 31 Dec 2015
Permit/Variation Number:
Year: Month: to | Period of Invalidation (hours) | Cumulated Invalidated Days in a Year | Comments
Date:
NOTES:
(a) Compliance in Chapter III of the IED is on the basis of validated hourly averages, measured by continuous monitors (except where discontinuous exemption applies). And confidence intervals are incorporated to convert the measured hourly value into a validated measurement for the purpose of compliance assessment. However, any day in which more than 3 hourly average values are invalid (due to malfunction or maintenance of the continuous measurement system) shall be invalidated for the purpose of compliance assessment. If more than 10 days are invalid over a year the operator shall, within 28 days of becoming aware of this fact, review the causes of the invalidations and submit to the Environment Agency for approval, proposals for measures to improve the reliability of the continuous measurement systems, including a timetable for the implementation of those measures; and implement the approved proposals.
Signed on behalf of the Operator by: | ……………..……………………………………..
Date of return: | ……………..……………………………………..

## (Not Req)IED BD1
RELEASES TO AIR
QUARTERLY RETURN
CUMULATIVE ROLLING MALFUNCTION AND BREAKDOWN HOURS (12 MONTH PERIOD)(a)
Operator: |  |  | Form: |  | IED BD1
Location: |  |  | Version/date: |  | V.2.1 31 Dec 2015
Permit/Variation Number:
Year: LCP: | SO2 |  | NOx |  | Dust |  | CO(c)
Month(b) | Malfunction (hours) | Breakdown (hours) | Malfunction (hours) | Breakdown (hours) | Malfunction (hours) | Breakdown (hours) | Malfunction (hours) | Breakdown (hours)
Month 1
Month 2
Month 3
Month 4
Month 5
Month 6
Month 7
Month 8
Month 9
Month 10
Month 11
Month 12
Annual cap (hours) | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
NOTES:
(a) Cumulative rolling malfunction and breakdown hours (12 month period) updated monthly
(b) Insert the relevant months for the preceding 12 month period, e.g., starting with March 2016
(c) Gas turbines with CO abatement only (columns may be deleted)
Signed on behalf of the Operator by: |  |  | ……………..………………………………………………..
Date of return: |  |  | ……………..………………………………………………..

## (Not Req)IED MF1
RELEASES TO AIR
RETURN OF DAILY MALFUNCTION AND BREAKDOWN DATA (a), (b), (c)
Operator:
Location: |  | Form: |  | IED MF1
Permit/Variation Number: |  | Version: |  | V.2.1 31 Dec 2015
LCP:
Type: | Malfunction/Breakdown /Normal Operation
Date: |  | SO2 | Excluded? | NOx | Excluded? | Dust | Excluded? | CO (d) | Excluded?
Hour | Start time | mg/m3 | Y/N | mg/m3 | Y/N | mg/m3 | Y/N | mg/m3 | Y/N
1 | 0:00
2 | 1:00
3 | 2:00
4 | 2:10
5 | 2:10
6 | 2:10
7 | 6:00
8 | 7:00
9 | 8:00
10 | 9:00
11 | 10:00
12 | 11:00
13 | 12:00
14 | 13:00
15 | 14:00
16 | 15:00
17 | 16:00
18 | 17:00
19 | 18:00
20 | 19:00
21 | 20:00
22 | 21:00
23 | 22:00
24 | 23:00
| Daily | Average | No. Hours | Average | No. Hours | Average | No. Hours | Average | No. Hours
Without data exclusion (All of the above data)
With data exclusion (Reportable data only)
Notes: | (a) Produce a return for each day which has data exclusion due to Malfunction or Breakdown
(b) All data based on hourly average validated concentrations (confidence interval subtracted)
(c) Reference conditions: mg/m3 dry, 273.15K, 101.325 kPa; Solid fuels 6% O2; Liquid and Gaseous fuels 3% O2; Gas turbines 15% O2
(d) Gas turbines with abatement only (columns may be deleted)
Signed on behalf of the Operator by: |  |  | ……………..………………………………………………..
Date of return: |  |  | ……………..………………………………………………..

## (Not Req)REM 1
RESOURCE EFFICIENCY METRICS
ANNUAL RETURN
CUMULATIVE ROLLING MALFUNCTION AND BREAKDOWN HOURS (12 MONTH PERIOD)(a)
Operator:
Permit/Variation Number:
Parameter | (a) | Units
Electricity Exported |  | GWhr
Heat Exported |  | GWhr
Mechanical Power Provided |  | GWhr
Fossil Fuel Energy Consumption |  | GWhr
Non-Fossil Fuel Consumption
Annual Operating Hours
Water Abstracted from Fresh Water Source
Water Abstracted from Borehole Source |  | m3
Water Abstracted from Estuarine Water Source |  | m3
Water Abstracted from Sea Water Source |  | m3
Water Abstracted from Mains Water Source |  | m3
Gross Total Water Used |  | m3
Net Water Used |  | m3
Hazardous Waste Transferred for Disposal at another Installation |  | t
Hazardous Waste Transferred for Recovery at another Installation |  | t
Non-Hazardous Waste Transferred for Disposal at another Installation |  | t
Non-Hazardous Waste Transferred for Recovery at another Installation |  | t
Waste Recovered to Quality Protocol Specification and Transferred Off-Site |  | t
Waste Transferred Directly Off-Site for Use under an exemption / position statement |  | t
NOTES:
(a) ) General note: Parameters should be reported as a decimal number to 2 decimal places.
Signed on behalf of the Operator by:
Date of return: