SOUTH WALES WOOD RECYCLING LTD
FIRE RISK ASSESSMENT

JULY 2017
CONTENTS

Introduction – Fire Risk Assessment 

Section 








   

1 Premises Particulars

2 General Statement of Policy

3


Management Systems
4


General Description of Premises

5 Fire Safety Systems within the premises 




6 Plan Drawing




       

7


Fire Hazards

8  


People at Risk

9 Means of Escape (Horizontal Evacuation)

10


Means of Escape (Vertical Evacuation)

11 Fire Safety Signs and Notices

12 Fire Warning System

13 Emergency lighting

14 Fire Fighting Equipment
15 Maintenance

16 Method of calling the Fire Service

17 Emergency Action Plan

18 Training

19 Record of Fire Safety Deficiencies

20 Significant Findings

21 Additional Hazards

	FIRE RISK ASSESSMENT

	1
	PREMISES PARTICULARS

	Premises Name: 
NEWPORT – COAL STORE
Tel no: 
George Harvey (SWWR) - 07771 484840
	Use of Premises

TREATMENT YARD AND STOARGE AREA


	
	Owner/Employer/Person in control of the workplace: South Wales Wood Recycling Ltd


	Date of Risk

Assessment: JULY 2017

	Date of

Review: July 2018 (unless changes to building/activities etc.)


	Name & relevant details of the person who carried out the Fire Risk Assessment

G Harvey – IOSH, COTC, WAMITAB  LEVEL 4



	2
	GENERAL STATEMENT OF POLICY

	Statement:
REFER TO COMPANY H&S POLICY STATEMENT
Signed:



Print Name:



Date:




	3
	MANAGEMENT SYSTEMS

	Commentary:
Planning:

The site has been inspected on numerous occasions by NRW and the South Wales Fire Service over the 18 months. At all times the current area has been deemed to be in compliance with all regulatory guidance and has effectively been operated as a regulated facility. Following discussions and agreements with NRW and the landowner, ABP, the area was agreed to be permitted. All activities undertaken will be identical to those undertaken previously. Consideration has been given to the NRW guidance fire prevention and mitigation plan (version 1 March 2016).
Organisation:

The Company is structured as that indicated within the PAS 402 Management System manual with an organogram depicting the set up and areas of responsibility.

Health & safety information is communicated via toolbox talks, notice boards, contact and periodic training arrangements.

Employees are made aware of fire arrangements by the fire action notices displayed within the buildings and contributing to periodic fire drills. It is also contained within their Safe Systems of Work booklets and delivered via team briefs.
Control:

The H&S manual and displayed documents/notices identify the responsibilities of those within the buildings (as appropriate) or via other appropriate means (i.e. tool box talk).
This can include: management, fire marshal, first aiders and other nominated persons.

Monitoring:

An external audit of the facilities will be performed, as required, on at least an annual basis by the H&S advisor/consultant and a report submitted to management. Any corrective/preventive actions will be adequately documented and closed out.
Other site monitoring includes a weekly review/record of fire precautions arrangements normally performed by the MD and/or a nominated person e.g. fire marshal.

Information is exchanged informally as it occurs and formally at the preset training days/management meetings.

Review:

All procedures are regularly reviewed via informal and/or formal arrangements and the appropriate actions taken to remediate/rectify.



	4
	GENERAL DESCRIPTION OF PREMISES

	Description:

The site is adjacent to an old Coal Store area within the Newport Docks site and a steel reel storage area. A manufacturing plant is also located to the south west, some 250 metres away. Otherwise the neighboring area is used for receipt and loading of various cargo and has been used as such for many years.
The site comprises a flat yard surfaced in impermeable hard standing over its entire surface and sitting at an elevation of 9m AOD.  Access to the site, is through a shared entrance and the permitted area will be cordoned off. The main access to the docks is controlled by a security cabin and gate and mobile security monitor the site 24hrs a day, 7 days per week.


	Occupancy

Times the Premises are in use (when operational): 6am to 6am
The Total Number of persons Employed

within the premises at any one time:  2
The Total Number of persons who may

resort to the premises at any one time: 4

	Size

Building footprint 
(Metres x Metres): N/A
Number of floors: N/A
Number of Stairs: N/A


	5
	FIRE SAFETY SYSTEMS WITHIN THE PREMISES

	Fire Warning System:  (i.e. automatic fire detection, break-glass system to BS 5839, other)
As there are no buildings the warning system would be via regular inspections and visual checks.


	Emergency Lighting:  (i.e. maintained/non-maintained, 1hr/3hr duration to BS 5266)
None

	Other:  (i.e. Sprinkler system to LPC rules BS 5306)
Unlimited water is available from the high pressure water hydrants on site should an issue arise. Additionally, extraction from the docks water would also be possible.
Fire engine or high pressure hoses will be available for use when material is being moved and / or rotated to ensure suppression is available in the event of a fire. Heavy plant and machinery (loading shovel and excavator) should also be on hand to assist with dealing with any issues.
FRS and NRW have contact details to ensure that if there is an issue we can be contacted to mobilize if needed. Subject to the time of call received, response time for plant and machinery should be within a matter of hours if the site is not manned.


	6
	PLAN DRAWING

	See attached - Site plan detailing:

1) Stockpile locations, sizes and breaks

2) Quarantine area

3) Access areas for fire department

4) Location of water supplies



	7
	IDENTIFY FIRE HAZARDS

	Sources of Ignition:

Plant and Machinery – daily maintenance and servicing

Stockpiles – regular rotation and movement

Waste material – permit control and inspections

Arson – site security at entrance and routine physical monitoring 24hrs per day
 

	Sources of Fuel:

Flammable liquids stored/used within the site – COSHH assessment and no storage on site.
Waste materials to be stored largely in line with NRW Fire prevention and mitigation guidance (version 1 March 2016) in addition to any additional recommendations from FRS and NRW and subject to amendments following site conditions. 
Waste material to consist of recycled waste wood.


	Work Processes:

The site will hold approximately 5,000tns of recycled waste wood on site.
We are committed to continually improving our environmental, health & safety and quality aspects of our operation by operating to the clauses laid out in PAS 402:2013.

Activities. 
· Stockpiling of the product shall be largely in accordance with current guidelines
· Stockpile height will vary but should not exceed 5m high at any point.
· Stockpiles will be at least 6m from any building.
· Stockpiles should not be stacked within 6m of any other stockpile or close to any combustible materials or ignition points.
· Pedestrians will be restricted from the working area.
· Vehicles / machinery should not be allowed to park in the vicinity of the stockpiles. This will be a minimum of 20m from any stockpile.
· Product will be rotated utilizing an excavator and loading shovel. It will be pulled down and pushed up. This will be done for the length of each pile.

· The product should be monitored on a regular basis for temperature. This would normally occur if any material remains on site for longer than 3 months without moving. Where temperature exceeds 65 degrees Celsius, the material must be pulled down and spread and allowed to cool and further regular turning of the product shall be carried out to aid cooling. All monitoring, inspections and action taken shall be recorded. Temperature readings will be undertaken as a precautionary measure on a monthly basis by heavy plant to remove material in the center of the stack and readings taken via a laser. Visual inspections will be made daily also to check for stability and debris as well as uncharacteristic behavior (for example, shimmering / steam / smoke).
· Hot spots will be removed using heavy plant and machinery (combination of an excavator and loading shovel), spread out and allowed to cool. They will then be placed back into stockpile once below 20 degrees Celsius or removed from site for processing
· All personnel involved in the handling of the product shall undergo appropriate training and instruction relative to their roles and receive regular tool box talks, especially where there is a change of personnel, procedures or equipment.
· In addition to the mandatory site PPE, goggles and masks shall be provided for use in dusty / windy conditions.
· All personnel should be reminded of the site rules on smoking and hygiene.
· All hotwork to be carried out on site shall be under permit to work conditions

Addition measures / detail:

Storage Methods

· Stockpile heights will vary but should not exceed 5m high and any stack will be kept at least 6m away from any structure or flammable material store.
· The maximum tonnage storage capacity in each pile will be no more than 1,750tns at any one time. Piles should be no more than 50m x 20m x 5m, but may vary subject to site operational demands.
· Access to all areas of the site will be maintained always.
· Should storage limits be reached or issues on site prevent material from coming in, material should be diverted to an alternate facility as determined. This will be known through reference to the material record sheets.
Preventative Action

· The stacks will be routinely monitored by staff and any ‘unusual behavior’ (i.e. shimmering / steam / smoke) reported and acted upon. The site will also be routinely inspected.

· Staff and contractors on site will follow safe working practices when site becomes functional in the near future.

· Visitors will follow the correct safety and fire prevention procedures

· The area is strictly non smoking with appropriate signage erected.

· All plant and machinery is regularly maintained and never parked near the stockpiles. Plant and machinery is only ever operated by suitably trained operatives.

Fire Prevention / Response Plan

· Fire risk assessment will be undertaken and an emergency response plan prepared.

· The site will observe health and safety procedures and comply with fire regulations. Staff will be suitably trained.

· Advice will be sought from local Fire & Rescue Service on the appropriate provision of fire extinguishing devices

· A traffic light system of action i.e. where green reflects a straight forward extinguish event using hand held fire extinguishers. Amber will require use of the fire engine and / or heavy plant and machinery to further isolate material or move it to the quarantine area and a red alert will be a controlled burn event where it is deemed too dangerous for personnel and plant and machinery to be used. In a red event scenario, the focus will be on damping down adjacent piles to control the radiant heat and prevent spread of the fire. This will be achieved by regular but controlled dowsing of the piles with water or potentially moving the potentially at risk material with heavy plant and machinery. Adjacent material may also be moved out of the way using the heavy plant and machinery.
Fire fighting strategy
· Call 999 and ask for Fire Brigade and provide site location as per fire safety signs.
· Evaluate situation on attendance in line with traffic light system (green, amber or red)

· Inform management and staff
· Provided it is safe to do so, ensure safe access to water and affected area is secured and ready necessary pipes / hoses and fire engine

· Await assistance unless green scenario and only proceed to tackle fire in this instance if it is safe to do so

· If an amber scenario is presented, do not attempt to tackle the situation on your own. Await for attendance by the FRS or site management at the fire assembly point ensuring all personnel are present and accounted for.
· Site management and FRS will make decision based on most appropriate way to tackle the fire given specific circumstances at the time.
Note: In the event that the third party realise there is a fire on site by monitoring the CCTV / inspection, they have direct contacts for all site management and are advised to inform the emergency services also.



	Structural features that could promote the spread of fire:




	8
	IDENTIFY PEOPLE AT RISK

	Identify and specify the likely location of people at significant risk in case of fire, indicating why they are at risk, and what control’s are or need to be in place:

Employees: 

Minimal employee presence on site and in event of fire employee will meet at welfare cabin. Access/egress to and from site is controlled via site personnel when operational. Doors and gates are locked and only employees have keys. 
The Company is not aware of any disabilities etc which could cause issues under emergency situations.

Visitors etc:

Access is controlled via security (when operational) / barrier and site instruction govern the activities allowed on site. All visitors are supervised and accompanied when required.

Contractors:
Contractors made aware of emergency arrangements and an assessment made upon the work to be performed. 
Limited lone working is performed however there is a lone working system and RA for such.
Impact of a fire on the immediate and surrounding area:
1) The impact depends on the nature of the fire and will be governed by site specific and event specific factors at the time, including the weather.
2) In view of the controls in place on the stockpile management, the nature of the material, heavy plant and machinery and water availability, any foreseeable incident should be able to be concluded quickly thereby minimizing impact on the local environment and community. A specific time cannot be provided for dealing with an issue due to the unknown variables (weather, tonnage affected, fire service response / decisions) though we would aim to meet the targets set within the guidance.

3) There are no public railways or power lines in the vicinity and we do not believe that there would be an impact on the road network.
4) In terms of residential premises and businesses locally, again, this will be wholly dependent on the site conditions at the time. It would be highly unlikely, due to the control measures and distances involved, if premises had to be evacuated though advice would be to shut windows and doors if affected.
5) In respect of the River Usk, in the highly unlikely event of any soot landing on the estuary, it is one of the largest tidal estuaries in the UK and this is a significant mitigating factor for any potential environmental risk.

6) The water run-off will be dependent on the nature of the incident and should all be contained within the sealed drainage system. It is wholly dependent on a case by case basis.




	9
	MEANS OF ESCAPE – HORIZONTAL EVACUATION

	Commentary:

· Fire hazards are controlled by employees, stock management and site management via cursory inspections
· Emergency and fire arrangements are recorded as per the documented system included within this plan.

· Induction records are used for all employees particularly for new and temporary site users. 
· Housekeeping is part of the regular site monitoring/checking arrangements and immediate action taken as required – personnel are to be continually briefed on storage and access needs.

· Stockpiles are kept clear of access routes and away from buildings.



	10
	MEANS OF ESCAPE – VERTICAL EVACUATION

	Commentary:

N / A


	11
	FIRE SAFETY SIGNS & NOTICES

	Commentary:
The emergency plan is to be updated in conjunction with this RA.



	12
	FIRE WARNING SYSTEM

	Commentary:

As there are no buildings the warning system would be via regular inspections and visual checks.


	13
	EMERGENCY LIGHTING SYSTEM

	Commentary:

N / A


	14
	FIRE FIGHTING EQUIPMENT

	Commentary:

A fire engine could be available on site if there are any issues but it is envisages that the high pressure water mains should be sufficient. A pump could also be available to extract water from the dock if additional supplies were required.

Any fire water will be recirculated back onto the material to prevent any fire water run off / tanked off site. Bunds will also be placed in effect should the need arise. Existing firefighting equipment has been approved by a competent installation company and is subject to annual checks and upgrades as appropriate.


Recommended maintenance schedule

	Equipment
	Period
	Action

	
	
	

	Fire engine

	Monthly
	Check all systems for state of repair and operation. Repair or replace defective units Test operation of systems

	
	
	

	
	Annually
	Full check and test of system by competent service engineer.

	
	
	

	
	
	

	
	
	

	
	
	

	Fire-fighting equipment including

hose reels.
	Weekly


	Check all extinguishers including

hose reels for correct installation

and apparent working order.

	
	
	

	
	Annually


	Full check and test by competent

service engineer.


	15
	MANAGEMENT - MAINTENACE

	Is there a maintenance programme for the fire safety provisions in the premises 
Yes / No

Commentary: A fire log book type recording system (site diary) is in use


	Are regular checks of fire resisting doors, walls & partitions carried out 
Yes / No

Commentary: N / A


	Are regular checks of escape routes & exit doors carried out
Yes / No

Commentary: N /A


	Are regular checks of fire safety signs carried out
Yes / No
Commentary: N / A


	Is there a maintenance regime for the fire warning system
Yes / No
Commentary: N / A


	Is there a maintenance regime for the emergency lighting system
Yes / No
Commentary: N / A


	Is there maintenance of the fire fighting equipment (By competent persons?)
Yes / No
Commentary: Yes - As per fire log record and per competent engineers


	Are records kept & their location identified
Yes / No
Commentary: As per fire log record and per competent engineers



	16
	METHOD FOR CALLING THE FIRE SERVICE

	Specify:
Calls must be made from site mobile phones and ‘999’ dialed – request Fire Service.


	17
	EMERGENCY ACTION PLAN (EAP)

	Commentary:

This is a separate document appended to this fire RA.


	18
	TRAINING

	Commentary:

· The existing EAP is kept in the site cabin.
· The induction form has also been updated to reflect additional fire precautions and awareness to include contractors who must inform site management of any activities employed which could compromise the fire precautions and RA e.g. power use, flammable materials, means of escape etc. 

· Fire training is also received via the evacuation and fire drills performed at least on an annual basis.

· Fire marshals are to be re-established/expanded upon with nominated persons being given that task and awareness/training given to follow this plan and the EAP



	19
	FIRE SAFETY DEFICIENCIES TO BE RECTIFIED

	Deficiency/Rectification


	Priority


	Date to be

Rectified


	Date

Rectified



	
	
	
	


	20
	SIGNIFICANT FINDINGS

	Significant Finding


	Control Measure/Action



	*Insert additional pages as required


	


	21
	ADDITIONAL HAZARDS

	Specify:




